## General
Excel file version | v2.0
Name | ieee13pv
Frequency (Hz) | 60
Power Base (MVA) | 100

## Voltage Source
Type
PositiveSeqVsource
SinglePhaseVsource
ThreePhaseShortCircuitVsource
ThreePhaseSequentialVsource
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive Sequence Voltage Source
ID | Bus | Voltage (pu) | Angle (deg) | Rs (pu) | Xs (pu)
End of Positive Sequence Voltage Source
Single-Phase Voltage Source
ID | Bus1 | Voltage (V) | Angle (deg) | Rs (Ohm) | Xs (Ohm)
End of Single-Phase Voltage Source
Three-Phase Voltage Source with Short-Circuit Level Data
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | SC1ph (MVA) | SC3ph (MVA)
End of Three-Phase Voltage Source with Short-Circuit Level Data
Three-Phase Voltage Source with Sequential Data
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | R1 (Ohm) | X1 (Ohm) | R0 (Ohm) | X0 (Ohm)
VS_source | sourcebus_A | sourcebus_B | sourcebus_C | 115 | 30 | 0.16038 | 0.64151 | 0.1796 | 0.53881
End of Three-Phase Voltage Source with Sequential Data

## Load
Type
PositiveSeqZload | ThreePhaseZIPLoad
PositiveSeqPload
PositiveSeqIload
SinglePhaseZIPLoad
TwoPhaseZIPLoad
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Constant Imepedance Load
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Constant Imepedance Load
Positive-Sequence Constant Power Load
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Constant Power Load
Positive-Sequence Constant Current Load
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Constant Current Load
Single-Phase ZIP Load
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | P1 (kW) | Q1 (kVAr)
LD_611 | 1 | 4.16 | 0.12 | wye | 0 | 100 | 0 | 0 | 611_C | 170 | 80
LD_634a | 1 | 0.48 | 0.12 | wye | 0 | 0 | 100 | 0 | 634_A | 160 | 110
LD_634b | 1 | 0.48 | 0.12 | wye | 0 | 0 | 100 | 0 | 634_B | 120 | 90
LD_634c | 1 | 0.48 | 0.12 | wye | 0 | 0 | 100 | 0 | 634_C | 120 | 90
LD_645 | 1 | 4.16 | 0.12 | wye | 0 | 0 | 100 | 0 | 645_B | 170 | 125
LD_646 | 1 | 4.16 | 0.12 | delta | 100 | 0 | 0 | 0 | 646_B | 230 | 132
LD_652 | 1 | 4.16 | 0.12 | wye | 100 | 0 | 0 | 0 | 652_A | 128 | 86
LD_670a | 1 | 4.16 | 0.12 | wye | 0 | 0 | 100 | 0 | 670_A | 17 | 10
LD_670b | 1 | 4.16 | 0.12 | wye | 0 | 0 | 100 | 0 | 670_B | 66 | 38
LD_670c | 1 | 4.16 | 0.12 | wye | 0 | 0 | 100 | 0 | 670_C | 117 | 68
LD_675a | 1 | 4.16 | 0.12 | wye | 0 | 0 | 100 | 0 | 675_A | 485 | 190
LD_675b | 1 | 4.16 | 0.12 | wye | 0 | 0 | 100 | 0 | 675_B | 68 | 60
LD_675c | 1 | 4.16 | 0.12 | wye | 0 | 0 | 100 | 0 | 675_C | 290 | 212
LD_692 | 1 | 4.16 | 0.12 | delta | 0 | 100 | 0 | 0 | 692_C | 170 | 151
End of SinglePhase ZIP Load
Two-Phase ZIP Load
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr)
LD_house | 1 | 0.208 | 0.12 | wye | 0 | 0 | 100 | 0 | house_s1 | house_s2 | 2.5 | 1.5494 | 2.5 | 1.5494
LD_pv_house | 1 | 0.208 | 0.12 | wye | 0 | 100 | 0 | 0 | house_s1 | house_s2 | -2 | 0 | -2 | 0
LD_bat_house | 1 | 0.208 | 0.12 | wye | 0 | 100 | 0 | 0 | house_s1 | house_s2 | 2.5 | 0 | 2.5 | 0
End of TwoPhase ZIP Load
Three-Phase ZIP Load
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | Bus3 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
LD_671 | 1 | 4.16 | 0.12 | delta | 0 | 0 | 100 | 0 | 671_A | 671_B | 671_C | 385 | 220 | 385 | 220 | 385 | 220
LD_pv_school | 1 | 0.48 | 0.12 | wye | 0 | 100 | 0 | 0 | 634_A | 634_B | 634_C | -80 | 0 | -80 | 0 | -80 | 0
LD_bat_school | 1 | 0.48 | 0.12 | wye | 0 | 100 | 0 | 0 | 634_A | 634_B | 634_C | 33.3333 | 0 | 33.3333 | 0 | 33.3333 | 0
End of ThreePhase ZIP Load

## Shunt
Type
PositiveSeqShunt
SinglePhaseShunt
TwoPhaseShunt
ThreePhaseShunt
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive Sequence Shunt
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Shunt
Single-Phase Shunt
ID | Status | kV (ph-gr RMS) | Bus1 | P1 (kW) | Q1 (kVAr)
SH_cap2 | 1 | 2.4 | 611_C | 0 | 100
End of Single-Phase Shunt
Two-Phase Shunt
ID | Status1 | Status2 | kV (ph-gr RMS) | Bus1 | Bus2 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr)
End of Two-Phase Shunt
Three-Phase Shunt
ID | Status1 | Status2 | Status3 | kV (ph-gr RMS) | Bus1 | Bus2 | Bus3 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
SH_cap1 | 1 | 1 | 1 | 2.4018 | 675_A | 675_B | 675_C | 0 | 200 | 0 | 200 | 0 | 200
End of Three-Phase Shunt

## Line
Type
PositiveSeqLine
SinglePhaseLine
TwoPhaseLine
ThreePhaseLineFullData
ThreePhaseLineSequentialData
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Line
ID | Status | From bus | To bus | R (pu) | X (pu) | B (pu)
End of Positive-Sequence Line
Single-Phase Line
ID | Status | Length | From1 | To1 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | b11 (uS/length_unit)
LN_684611 | 1 | 91.44 | tap_C | 611_C | 0.00082593 | 0.0008373 | 0
LN_684652 | 1 | 243.84 | 684_A | 652_A | 0.00083419 | 0.00031839 | 0.055283
End of Single-Phase Line
Two-Phase Line
ID | Status | Length | From1 | From2 | To1 | To2 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit)
LN_632645 | 1 | 152.4 | 632_C | 632_B | 645_C | 645_B | 0.00082257 | 0.00084314 | 0.00012838 | 0.00028527 | 0.00082605 | 0.00083705 | 0 | 0 | 0
LN_645646 | 1 | 91.44 | 645_C | 645_B | 646_C | 646_B | 0.00082257 | 0.00084314 | 0.00012838 | 0.00028527 | 0.00082605 | 0.00083705 | 0 | 0 | 0
LN_671684 | 1 | 91.44 | 671_A | 671_C | 684_A | 684_C | 0.00082257 | 0.00084314 | 0.00012838 | 0.00028527 | 0.00082605 | 0.00083705 | 0 | 0 | 0
End of Two-Phase Line
Three-Phase Line with Full Data
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | r31 (Ohm/length_unit) | x31 (Ohm/length_unit) | r32 (Ohm/length_unit) | x32 (Ohm/length_unit) | r33 (Ohm/length_unit) | x33 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit) | b31 (uS/length_unit) | b32 (uS/length_unit) | b33 (uS/length_unit)
LN_632633 | 1 | 152.4 | 632_A | 632_B | 632_C | 633_A | 633_B | 633_C | 0.00046764 | 0.00073409 | 9.538e-05 | 0.00023917 | 0.00046447 | 0.00074459 | 9.6934e-05 | 0.00031174 | 9.8177e-05 | 0.00026321 | 0.00046205 | 0.0007526 | 0 | 0 | 0 | 0 | 0 | 0
LN_632670 | 1 | 203.3016 | mid_A | mid_B | mid_C | 670_A | 670_B | 670_C | 0.00021531 | 0.00063249 | 9.538e-05 | 0.00023917 | 0.00020971 | 0.00065107 | 9.8177e-05 | 0.00026321 | 9.6934e-05 | 0.00031174 | 0.00021214 | 0.00064299 | 0 | 0 | 0 | 0 | 0 | 0
LN_650632 | 1 | 609.6 | rg60_A | rg60_B | rg60_C | 632_A | 632_B | 632_C | 0.00021531 | 0.00063249 | 9.538e-05 | 0.00023917 | 0.00020971 | 0.00065107 | 9.8177e-05 | 0.00026321 | 9.6934e-05 | 0.00031174 | 0.00021214 | 0.00064299 | 0 | 0 | 0 | 0 | 0 | 0
LN_670671 | 1 | 406.2984 | 670_A | 670_B | 670_C | 671_A | 671_B | 671_C | 0.00021531 | 0.00063249 | 9.538e-05 | 0.00023917 | 0.00020971 | 0.00065107 | 9.8177e-05 | 0.00026321 | 9.6934e-05 | 0.00031174 | 0.00021214 | 0.00064299 | 0 | 0 | 0 | 0 | 0 | 0
LN_671680 | 1 | 304.8 | 671_A | 671_B | 671_C | 680_A | 680_B | 680_C | 0.00021531 | 0.00063249 | 9.538e-05 | 0.00023917 | 0.00020971 | 0.00065107 | 9.8177e-05 | 0.00026321 | 9.6934e-05 | 0.00031174 | 0.00021214 | 0.00064299 | 0 | 0 | 0 | 0 | 0 | 0
LN_692675 | 1 | 152.4 | 692_A | 692_B | 692_C | 675_A | 675_B | 675_C | 0.00049195 | 0.00027238 | 0.00019789 | 1.7202e-05 | 0.00048569 | 0.0002465 | 0.00017613 | -1.1446e-05 | 0.00019789 | 1.7202e-05 | 0.00049195 | 0.00027238 | 0.08994 | 0 | 0.08994 | 0 | 0 | 0.08994
End of Three-Phase Line with Full Data
Three-Phase Line with Sequential Data
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | R0 (Ohm/length_unit) | X0 (Ohm/length_unit) | R1 (Ohm/length_unit) | X1 (Ohm/length_unit) | B0 (uS/length_unit) | B1 (uS/length_unit)
End of Three-Phase Line with Sequential Data

## Transformer
Type
PositiveSeq2wXF
PositiveSeq3wXF
Multiphase2wXF
Multiphase2wXFMutual
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence 2W Transformer
ID | Status | From bus | To bus | R (pu) | Xl (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Phase Shift (deg)
End of Positive-Sequence 2W Transformer
Positive-Sequence 3W Transformer
ID | Status | Bus1 | Bus2 | Bus3 | R_12 (pu) | Xl_12 (pu) | R_23 (pu) | Xl_23 (pu) | R_31 (pu) | Xl_31 (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Ratio W3 (pu) | Phase Shift W1 (deg) | Phase Shift W2 (deg) | Phase Shift W3 (deg)
End of Positive-Sequence 3W Transformer
Multiphase 2W Transformer
ID | Status | Number of phases | Bus1_A | Bus1_B | Bus1_C | V1 (kV) | S_base1 (kVA) | Conn. type1 | Bus2_A | Bus2_B | Bus2_C | V2 (kV) | S_base2 (kVA) | Conn. type2 | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | X (pu) | RW1 (pu) | RW2 (pu)
XF_sub | 1 | 3 | sourcebus_A | sourcebus_B | sourcebus_C | 115 | 5000 | delta | 650_A | 650_B | 650_C | 4.16 | 5000 | wye | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8e-05 | 5e-06 | 5e-06
XF_xfm1 | 1 | 3 | xf1_A | xf1_B | xf1_C | 4.16 | 500 | wye | 634_A | 634_B | 634_C | 0.48 | 500 | wye | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.0055 | 0.0055
XF_Reg:reg1 | 1 | 1 | brkr_A |  |  | 4.1569 | 1666 | wye | rg60_A |  |  | 4.1569 | 1666 | wye | 10 | 0 | 0 | -16 | 16 | 10 | 10 | 0.00014142 | 5e-05 | 5e-05
XF_Reg:reg2 | 1 | 1 | brkr_B |  |  | 4.1569 | 1666 | wye | rg60_B |  |  | 4.1569 | 1666 | wye | 8 | 0 | 0 | -16 | 16 | 10 | 10 | 0.00014142 | 5e-05 | 5e-05
XF_Reg:reg3 | 1 | 1 | brkr_C |  |  | 4.1569 | 1666 | wye | rg60_C |  |  | 4.1569 | 1666 | wye | 10 | 0 | 0 | -16 | 16 | 10 | 10 | 0.00014142 | 5e-05 | 5e-05
XF_tpoletop:tpoletop | 1 | 1 | xfbus_tpoletop_B |  |  | 4.1569 | 5 | wye | house_s1 |  |  | 0.20785 | 5 | wye | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013793 | 0.006 | 0.006
XF_tpoletop:tpoletop | 1 | 1 | xfbus_tpoletop_B |  |  | 4.1569 | 5 | wye | house_s2 |  |  | 0.20785 | 5 | wye | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013793 | 0.006 | 0.006
End of Multiphase 2W Transformer
Multiphase 2W Transformer with Mutual Impedance
ID | Status | Number of phases | Bus1_A | Bus1_B | Bus1_C | V1 (kV) | S_base1 (kVA) | Conn. type1 | Bus2_A | Bus2_B | Bus2_C | V2 (kV) | S_base2 (kVA) | Conn. type2 | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | Z0 leakage (pu) | Z1 leakage (pu) | X0/R0 | X1/R1 | No Load Loss (kW)
XF_tpoletop:tpoletop | 1 | 1 | 670_B |  |  | 4.1569 | 5 | wye | xfbus_tpoletop_B |  |  | 4.1569 | 5 | wye | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014694 | 0.014694 | 2.2355 | 2.2355 | 0.01
End of Multiphase 2W Transformer with Mutual Impedance

## Bus
Bus | Base Voltage (V) | Initial Vmag | Unit (V, pu) | Angle (deg) | Type
611_C | 2401.7771 | 1 | pu | 120 | PQ
632_A | 2401.7771 | 1 | pu | 0 | PQ
632_B | 2401.7771 | 1 | pu | -120 | PQ
632_C | 2401.7771 | 1 | pu | 120 | PQ
633_A | 2401.7771 | 1 | pu | 0 | PQ
633_B | 2401.7771 | 1 | pu | -120 | PQ
633_C | 2401.7771 | 1 | pu | 120 | PQ
634_A | 277.1281 | 1 | pu | 0 | PQ
634_B | 277.1281 | 1 | pu | -120 | PQ
634_C | 277.1281 | 1 | pu | 120 | PQ
645_B | 2401.7771 | 1 | pu | -120 | PQ
645_C | 2401.7771 | 1 | pu | 120 | PQ
646_B | 2401.7771 | 1 | pu | -120 | PQ
646_C | 2401.7771 | 1 | pu | 120 | PQ
650_A | 2401.7771 | 1 | pu | 0 | PQ
650_B | 2401.7771 | 1 | pu | -120 | PQ
650_C | 2401.7771 | 1 | pu | 120 | PQ
652_A | 2401.7771 | 1 | pu | 0 | PQ
670_A | 2401.7771 | 1 | pu | 0 | PQ
670_B | 2401.7771 | 1 | pu | -120 | PQ
670_C | 2401.7771 | 1 | pu | 120 | PQ
671_A | 2401.7771 | 1 | pu | 0 | PQ
671_B | 2401.7771 | 1 | pu | -120 | PQ
671_C | 2401.7771 | 1 | pu | 120 | PQ
675_A | 2401.7771 | 1 | pu | 0 | PQ
675_B | 2401.7771 | 1 | pu | -120 | PQ
675_C | 2401.7771 | 1 | pu | 120 | PQ
680_A | 2401.7771 | 1 | pu | 0 | PQ
680_B | 2401.7771 | 1 | pu | -120 | PQ
680_C | 2401.7771 | 1 | pu | 120 | PQ
684_A | 2401.7771 | 1 | pu | 0 | PQ
684_C | 2401.7771 | 1 | pu | 120 | PQ
692_B | 2401.7771 | 1 | pu | -120 | PQ
692_A | 2401.7771 | 1 | pu | 0 | PQ
692_C | 2401.7771 | 1 | pu | 120 | PQ
brkr_A | 2401.7771 | 1 | pu | 0 | PQ
brkr_B | 2401.7771 | 1 | pu | -120 | PQ
brkr_C | 2401.7771 | 1 | pu | 120 | PQ
house_s2 | 120.0889 | 1 | pu | 180 | PQ
house_s1 | 120.0889 | 1 | pu | 0 | PQ
mid_A | 2401.7771 | 1 | pu | 0 | PQ
mid_B | 2401.7771 | 1 | pu | -120 | PQ
mid_C | 2401.7771 | 1 | pu | 120 | PQ
rg60_A | 2401.7771 | 1 | pu | 0 | PQ
rg60_B | 2401.7771 | 1 | pu | -120 | PQ
rg60_C | 2401.7771 | 1 | pu | 120 | PQ
sourcebus_A | 66395.281 | 1 | pu | 0 | SLACK
sourcebus_B | 66395.281 | 1 | pu | -120 | SLACK
sourcebus_C | 66395.281 | 1 | pu | 120 | SLACK
tap_C | 2401.7771 | 1 | pu | 120 | PQ
xf1_A | 2401.7771 | 1 | pu | 0 | PQ
xf1_B | 2401.7771 | 1 | pu | -120 | PQ
xf1_C | 2401.7771 | 1 | pu | 120 | PQ
xfbus_tpoletop_B | 2400 | 1 | pu | -120 | PQ

## Switch
From Bus | To Bus | ID | Status
650_A | brkr_A | SW_brkr1_A | 1
650_B | brkr_B | SW_brkr1_B | 1
650_C | brkr_C | SW_brkr1_C | 1
633_A | xf1_A | SW_fuse1_A | 1
633_B | xf1_B | SW_fuse1_B | 1
633_C | xf1_C | SW_fuse1_C | 1
671_A | 692_A | SW_671692_A | 1
671_B | 692_B | SW_671692_B | 1
671_C | 692_C | SW_671692_C | 1
684_C | tap_C | SW_sect1_C | 1
632_A | mid_A | SW_rec1_A | 1
632_B | mid_B | SW_rec1_B | 1
632_C | mid_C | SW_rec1_C | 1