## General
Excel file version | v2.0
Name | j1
Frequency (Hz) | 60
Power Base (MVA) | 100

## Voltage Source
Positive Sequence Voltage Source
ID | Bus | Voltage (pu) | Angle (deg) | Rs (pu) | Xs (pu)
End of Positive Sequence Voltage Source
Single-Phase Voltage Source
ID | Bus1 | Voltage (V) | Angle (deg) | Rs (Ohm) | Xs (Ohm)
End of Single-Phase Voltage Source
Three-Phase Voltage Source with Short-Circuit Level Data
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | SC1ph (MVA) | SC3ph (MVA)
End of Three-Phase Voltage Source with Short-Circuit Level Data
Three-Phase Voltage Source with Sequential Data
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | R1 (Ohm) | X1 (Ohm) | R0 (Ohm) | X0 (Ohm)
source | s_A | s_B | s_C | 66.93 | 0 | 1.376 | 14.257 | 0.001 | 8.203
End of Three-Phase Voltage Source with Sequential Data

## Load
Positive-Sequence Constant Imepedance Load
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Constant Imepedance Load
Positive-Sequence Constant Power Load
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Constant Power Load
Positive-Sequence Constant Current Load
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Constant Current Load
Single-Phase ZIP Load
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | P1 (kW) | Q1 (kVAr)
10_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | 5998528541_C | 0.05 | 0
10_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18948_C | 0.05 | 0
12_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | 6093229888_A | 49.95 | 40.6
12_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b19028_A | 49.95 | 40.6
32_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b24504_C | 78.95 | 56.9
32_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4725_C | 78.95 | 56.9
36_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b32783_B | 22.7 | 15.45
36_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4888_B | 22.7 | 15.45
48_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b47846_C | 61.9 | 43.55
48_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18967_C | 61.9 | 43.55
5_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | 5912527743_A | 23.85 | 17.65
5_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b2630_A | 23.85 | 17.65
62_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b52275_C | 15.1 | 10.25
62_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b19052_C | 15.1 | 10.25
64_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b56685_B | 69.85 | 45.55
64_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b43438_B | 69.85 | 45.55
65_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b57691_A | 22.85 | 17
65_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b19028_A | 22.85 | 17
66_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b58809_C | 13.65 | 9.35
66_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b19042_C | 13.65 | 9.35
End of SinglePhase ZIP Load
Two-Phase ZIP Load
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr)
23_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b19028_A | b19028_B | 19.7 | 13.975 | 19.7 | 13.975
23_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18967_A | b18967_B | 19.7 | 13.975 | 19.7 | 13.975
38_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b41878_A | b41878_B | 86 | 62.35 | 86 | 62.35
38_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b19028_A | b19028_B | 86 | 62.35 | 86 | 62.35
39_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b43438_A | b43438_B | 26 | 19.225 | 26 | 19.225
39_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b41878_A | b41878_B | 26 | 19.225 | 26 | 19.225
End of TwoPhase ZIP Load
Three-Phase ZIP Load
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | Bus3 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
11_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18858_A | b18858_B | b18858_C | 47.4 | 36.05 | 47.4 | 36.05 | 47.4 | 36.05
11_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | 6022828946_A | 6022828946_B | 6022828946_C | 47.4 | 36.05 | 47.4 | 36.05 | 47.4 | 36.05
13_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b19183_A | b19183_B | b19183_C | 3.5833 | 2.7167 | 3.5833 | 2.7167 | 3.5833 | 2.7167
13_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b13649_A | b13649_B | b13649_C | 3.5833 | 2.7167 | 3.5833 | 2.7167 | 3.5833 | 2.7167
17_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4833_A | b4833_B | b4833_C | 0.05 | 0.16667 | 0.05 | 0.16667 | 0.05 | 0.16667
17_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18821_A | b18821_B | b18821_C | 0.05 | 0.16667 | 0.05 | 0.16667 | 0.05 | 0.16667
18_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4837_A | b4837_B | b4837_C | 1.4833 | 1.2333 | 1.4833 | 1.2333 | 1.4833 | 1.2333
18_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18829_A | b18829_B | b18829_C | 1.4833 | 1.2333 | 1.4833 | 1.2333 | 1.4833 | 1.2333
19_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18829_A | b18829_B | b18829_C | 51.1833 | 36.4167 | 51.1833 | 36.4167 | 51.1833 | 36.4167
19_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18858_A | b18858_B | b18858_C | 51.1833 | 36.4167 | 51.1833 | 36.4167 | 51.1833 | 36.4167
20_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | 6022828946_A | 6022828946_B | 6022828946_C | 0.1 | 0.066667 | 0.1 | 0.066667 | 0.1 | 0.066667
20_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18941_A | b18941_B | b18941_C | 0.1 | 0.066667 | 0.1 | 0.066667 | 0.1 | 0.066667
21_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18941_A | b18941_B | b18941_C | 2.1333 | 1.3667 | 2.1333 | 1.3667 | 2.1333 | 1.3667
21_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18948_A | b18948_B | b18948_C | 2.1333 | 1.3667 | 2.1333 | 1.3667 | 2.1333 | 1.3667
22_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18948_A | b18948_B | b18948_C | 7.4833 | 5.8333 | 7.4833 | 5.8333 | 7.4833 | 5.8333
22_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18967_A | b18967_B | b18967_C | 7.4833 | 5.8333 | 7.4833 | 5.8333 | 7.4833 | 5.8333
24_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4808_A | b4808_B | b4808_C | 8.7167 | 6.4167 | 8.7167 | 6.4167 | 8.7167 | 6.4167
24_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b19042_A | b19042_B | b19042_C | 8.7167 | 6.4167 | 8.7167 | 6.4167 | 8.7167 | 6.4167
25_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4760_A | b4760_B | b4760_C | 12.1833 | 8.8833 | 12.1833 | 8.8833 | 12.1833 | 8.8833
25_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b19052_A | b19052_B | b19052_C | 12.1833 | 8.8833 | 12.1833 | 8.8833 | 12.1833 | 8.8833
26_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4760_A | b4760_B | b4760_C | 4.2167 | 3.1333 | 4.2167 | 3.1333 | 4.2167 | 3.1333
26_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b19183_A | b19183_B | b19183_C | 4.2167 | 3.1333 | 4.2167 | 3.1333 | 4.2167 | 3.1333
28_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4837_A | b4837_B | b4837_C | 3.05 | 2.0333 | 3.05 | 2.0333 | 3.05 | 2.0333
28_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b23208_A | b23208_B | b23208_C | 3.05 | 2.0333 | 3.05 | 2.0333 | 3.05 | 2.0333
29_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b5213_A | b5213_B | b5213_C | 9.7833 | 14.3667 | 9.7833 | 14.3667 | 9.7833 | 14.3667
29_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b23283_A | b23283_B | b23283_C | 9.7833 | 14.3667 | 9.7833 | 14.3667 | 9.7833 | 14.3667
33_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b23283_A | b23283_B | b23283_C | 8.65 | 6.0167 | 8.65 | 6.0167 | 8.65 | 6.0167
33_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b2630_A | b2630_B | b2630_C | 8.65 | 6.0167 | 8.65 | 6.0167 | 8.65 | 6.0167
3_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4833_A | b4833_B | b4833_C | 0.05 | -0.38333 | 0.05 | -0.38333 | 0.05 | -0.38333
3_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | 5865228330a_A | 5865228330a_B | 5865228330a_C | 0.05 | -0.38333 | 0.05 | -0.38333 | 0.05 | -0.38333
40_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4588_A | b4588_B | b4588_C | 29.1667 | 20.6167 | 29.1667 | 20.6167 | 29.1667 | 20.6167
40_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4541_A | b4541_B | b4541_C | 29.1667 | 20.6167 | 29.1667 | 20.6167 | 29.1667 | 20.6167
41_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4602_A | b4602_B | b4602_C | 7.55 | 5.2667 | 7.55 | 5.2667 | 7.55 | 5.2667
41_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4588_A | b4588_B | b4588_C | 7.55 | 5.2667 | 7.55 | 5.2667 | 7.55 | 5.2667
42_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4725_A | b4725_B | b4725_C | 8.6833 | 6.3667 | 8.6833 | 6.3667 | 8.6833 | 6.3667
42_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4602_A | b4602_B | b4602_C | 8.6833 | 6.3667 | 8.6833 | 6.3667 | 8.6833 | 6.3667
43_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4602_A | b4602_B | b4602_C | 3.5 | 2.3333 | 3.5 | 2.3333 | 3.5 | 2.3333
43_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4619_A | b4619_B | b4619_C | 3.5 | 2.3333 | 3.5 | 2.3333 | 3.5 | 2.3333
44_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18829_A | b18829_B | b18829_C | 5.7667 | 4.0333 | 5.7667 | 4.0333 | 5.7667 | 4.0333
44_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b46703_A | b46703_B | b46703_C | 5.7667 | 4.0333 | 5.7667 | 4.0333 | 5.7667 | 4.0333
45_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b13649_A | b13649_B | b13649_C | 1.3667 | 0.9 | 1.3667 | 0.9 | 1.3667 | 0.9
45_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4725_A | b4725_B | b4725_C | 1.3667 | 0.9 | 1.3667 | 0.9 | 1.3667 | 0.9
46_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4808_A | b4808_B | b4808_C | 14.8167 | 10.8167 | 14.8167 | 10.8167 | 14.8167 | 10.8167
46_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4760_A | b4760_B | b4760_C | 14.8167 | 10.8167 | 14.8167 | 10.8167 | 14.8167 | 10.8167
47_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4808_A | b4808_B | b4808_C | 14.0167 | 10.0167 | 14.0167 | 10.0167 | 14.0167 | 10.0167
47_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b47668_A | b47668_B | b47668_C | 14.0167 | 10.0167 | 14.0167 | 10.0167 | 14.0167 | 10.0167
50_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4808_A | b4808_B | b4808_C | 15.2 | 11.6333 | 15.2 | 11.6333 | 15.2 | 11.6333
50_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4829_A | b4829_B | b4829_C | 15.2 | 11.6333 | 15.2 | 11.6333 | 15.2 | 11.6333
51_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4829_A | b4829_B | b4829_C | 0.11667 | 0.36667 | 0.11667 | 0.36667 | 0.11667 | 0.36667
51_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4832_A | b4832_B | b4832_C | 0.11667 | 0.36667 | 0.11667 | 0.36667 | 0.11667 | 0.36667
52_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4832_A | b4832_B | b4832_C | 0.05 | 0.11667 | 0.05 | 0.11667 | 0.05 | 0.11667
52_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4833_A | b4833_B | b4833_C | 0.05 | 0.11667 | 0.05 | 0.11667 | 0.05 | 0.11667
54_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4862_A | b4862_B | b4862_C | 7.1833 | 5.8167 | 7.1833 | 5.8167 | 7.1833 | 5.8167
54_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4808_A | b4808_B | b4808_C | 7.1833 | 5.8167 | 7.1833 | 5.8167 | 7.1833 | 5.8167
56_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4888_A | b4888_B | b4888_C | 4.75 | 4.4833 | 4.75 | 4.4833 | 4.75 | 4.4833
56_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4877_A | b4877_B | b4877_C | 4.75 | 4.4833 | 4.75 | 4.4833 | 4.75 | 4.4833
57_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4909_A | b4909_B | b4909_C | 8.3833 | 8.6833 | 8.3833 | 8.6833 | 8.3833 | 8.6833
57_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4888_A | b4888_B | b4888_C | 8.3833 | 8.6833 | 8.3833 | 8.6833 | 8.3833 | 8.6833
58_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b23283_A | b23283_B | b23283_C | 36.4 | 39.1 | 36.4 | 39.1 | 36.4 | 39.1
58_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4909_A | b4909_B | b4909_C | 36.4 | 39.1 | 36.4 | 39.1 | 36.4 | 39.1
59_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b23208_A | b23208_B | b23208_C | 9.4667 | 6.35 | 9.4667 | 6.35 | 9.4667 | 6.35
59_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b51854_A | b51854_B | b51854_C | 9.4667 | 6.35 | 9.4667 | 6.35 | 9.4667 | 6.35
60_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b5220_A | b5220_B | b5220_C | 1.4167 | 2.75 | 1.4167 | 2.75 | 1.4167 | 2.75
60_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b5213_A | b5213_B | b5213_C | 1.4167 | 2.75 | 1.4167 | 2.75 | 1.4167 | 2.75
61_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | feederhead_A | feederhead_B | feederhead_C | 0.13333 | 0.4 | 0.13333 | 0.4 | 0.13333 | 0.4
61_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b5220_A | b5220_B | b5220_C | 0.13333 | 0.4 | 0.13333 | 0.4 | 0.13333 | 0.4
63_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b4833_A | b4833_B | b4833_C | 54.0333 | 37.4333 | 54.0333 | 37.4333 | 54.0333 | 37.4333
63_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b56591_A | b56591_B | b56591_C | 54.0333 | 37.4333 | 54.0333 | 37.4333 | 54.0333 | 37.4333
69_1 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b18821_A | b18821_B | b18821_C | 0.73333 | 0.51667 | 0.73333 | 0.51667 | 0.73333 | 0.51667
69_2 | 1 | 12.47 | 0.12 | wye | 100 | 0 | 0 | 0 | b61161_A | b61161_B | b61161_C | 0.73333 | 0.51667 | 0.73333 | 0.51667 | 0.73333 | 0.51667
aggregate_load | 1 | 12.47 | 0.12 | wye | 0 | 100 | 0 | 0 | ls_bus_A | ls_bus_B | ls_bus_C | 1666.6667 | -338.4311 | 1666.6667 | -338.4311 | 1666.6667 | -338.4311
End of ThreePhase ZIP Load

## Shunt
Positive Sequence Shunt
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Shunt
Single-Phase Shunt
ID | Status | kV (ph-gr RMS) | Bus1 | P1 (kW) | Q1 (kVAr)
End of Single-Phase Shunt
Two-Phase Shunt
ID | Status1 | Status2 | kV (ph-gr RMS) | Bus1 | Bus2 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr)
End of Two-Phase Shunt
Three-Phase Shunt
ID | Status1 | Status2 | Status3 | kV (ph-gr RMS) | Bus1 | Bus2 | Bus3 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
b18944 | 1 | 1 | 1 | 7.1996 | b18941_A | b18941_B | b18941_C | 0 | 400 | 0 | 400 | 0 | 400
b4829-1 | 1 | 1 | 1 | 7.1996 | b4829_A | b4829_B | b4829_C | 0 | 200 | 0 | 200 | 0 | 200
b4862-1 | 1 | 1 | 1 | 7.1996 | b4862_A | b4862_B | b4862_C | 0 | 200 | 0 | 200 | 0 | 200
b4877-1 | 1 | 1 | 1 | 7.1996 | b4877_A | b4877_B | b4877_C | 0 | 200 | 0 | 200 | 0 | 200
b4909-1 | 1 | 1 | 1 | 7.1996 | b4909_A | b4909_B | b4909_C | 0 | 300 | 0 | 300 | 0 | 300
End of Three-Phase Shunt

## Line
Positive-Sequence Line
ID | Status | From bus | To bus | R (pu) | X (pu) | B (pu)
End of Positive-Sequence Line
Single-Phase Line
ID | Status | Length | From1 | To1 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | b11 (uS/length_unit)
1 | 1 | 1 | 5848128103_C | b13923_C | 0.0007005 | 0.00045212 | 0
10 | 1 | 1 | 5998528541_C | b18948_C | 0.00094684 | 0.00063584 | 0
12 | 1 | 1 | 6093229888_A | b19028_A | 0.00076312 | 0.0005738 | 0
14 | 1 | 1 | b13923_C | b19052_C | 0.00070596 | 0.0003515 | 0
15 | 1 | 1 | b14440_C | b4837_C | 0.00020267 | 0.00011131 | 0
16 | 1 | 1 | b17991_C | b4588_C | 0.00077858 | 0.00041116 | 0
2 | 1 | 1 | 5851228580_C | b35443_C | 0.00031612 | 0.00019346 | 0
27 | 1 | 1 | b22803_C | b13923_C | 0.00074754 | 0.00044928 | 0
30 | 1 | 1 | b23416_A | b23283_A | 0.00082929 | 0.00052453 | 0
31 | 1 | 1 | b24288_C | b22803_C | 0.0025134 | 0.0015308 | 0
32 | 1 | 1 | b24504_C | b4725_C | 0.0011401 | 0.00085415 | 0
34 | 1 | 1 | b29921_C | b5213_C | 0.00029043 | 0.00016978 | 0
35 | 1 | 1 | b31997_C | b24504_C | 0.00051849 | 0.00031747 | 0
36 | 1 | 1 | b32783_B | b4888_B | 0.00045724 | 0.00036681 | 0
37 | 1 | 1 | b35443_C | b13649_C | 0.00035101 | 0.00013733 | 0
48 | 1 | 1 | b47846_C | b18967_C | 0.0011036 | 0.00076186 | 0
5 | 1 | 1 | 5912527743_A | b2630_A | 0.00062081 | 0.00045476 | 0
6 | 1 | 1 | 5925528209a_C | b60868_C | 0.00079905 | 0.00050504 | 0
62 | 1 | 1 | b52275_C | b19052_C | 0.00076688 | 0.0004986 | 0
64 | 1 | 1 | b56685_B | b43438_B | 0.00040136 | 0.00014689 | 0
65 | 1 | 1 | b57691_A | b19028_A | 0.00042491 | 0.00035427 | 0
66 | 1 | 1 | b58809_C | b19042_C | 0.00022201 | 0.00012767 | 0
67 | 1 | 1 | b59935_A | b41878_A | 0.00061685 | 0.00046898 | 0
68 | 1 | 1 | b60868_C | b2630_C | 0.00056332 | 0.00043973 | 0
7 | 1 | 1 | 5962929303_B | b43438_B | 0.00062555 | 0.00025911 | 0
71 | 1 | 1 | b63378_C | b35443_C | 0.0019212 | 0.0011672 | 0
72 | 1 | 1 | g36748_A | b4541_A | 0.00018649 | 0.00022964 | 0
73 | 1 | 1 | g42394_C | b47983_C | 0.0004504 | 0.0002557 | 0
8 | 1 | 1 | 5967328881_B | 6022828946_B | 0.00095143 | 0.00050636 | 0
9 | 1 | 1 | 5988528387_C | b60868_C | 0.00060791 | 0.00037884 | 0
End of Single-Phase Line
Two-Phase Line
ID | Status | Length | From1 | From2 | To1 | To2 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit)
23 | 1 | 1 | b19028_A | b19028_B | b18967_A | b18967_B | 0.00091092 | 0.0008034 | 0.00013251 | 0.00020547 | 0.00091092 | 0.0008034 | 4.3633e-06 | -2.3972e-07 | 4.3633e-06
38 | 1 | 1 | b41878_A | b41878_B | b19028_A | b19028_B | 0.00095244 | 0.00070345 | 9.3701e-05 | 0.00021727 | 0.00095244 | 0.00070345 | 4.3633e-06 | -2.3972e-07 | 4.3633e-06
39 | 1 | 1 | b43438_A | b43438_B | b41878_A | b41878_B | 0.00046478 | 0.00037845 | 5.431e-05 | 0.00013286 | 0.00046478 | 0.00037845 | 4.3633e-06 | -2.3972e-07 | 4.3633e-06
End of Two-Phase Line
Three-Phase Line with Full Data
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | r31 (Ohm/length_unit) | x31 (Ohm/length_unit) | r32 (Ohm/length_unit) | x32 (Ohm/length_unit) | r33 (Ohm/length_unit) | x33 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit) | b31 (uS/length_unit) | b32 (uS/length_unit) | b33 (uS/length_unit)
End of Three-Phase Line with Full Data
Three-Phase Line with Sequential Data
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | R0 (Ohm/length_unit) | X0 (Ohm/length_unit) | R1 (Ohm/length_unit) | X1 (Ohm/length_unit) | B0 (uS/length_unit) | B1 (uS/length_unit)
11 | 1 | 1 | b18858_A | b18858_B | b18858_C | 6022828946_A | 6022828946_B | 6022828946_C | 4.5207 | 4.1197 | 2.4224 | 1.6371 | 6.2505e-12 | 7.4079e-12
13 | 1 | 1 | b19183_A | b19183_B | b19183_C | b13649_A | b13649_B | b13649_C | 0.18827 | 0.54346 | 0.05852 | 0.17168 | 6.2505e-12 | 7.4079e-12
17 | 1 | 1 | b4833_A | b4833_B | b4833_C | b18821_A | b18821_B | b18821_C | 0.05728 | 0.07204 | 0.01376 | 0.02672 | 6.2505e-12 | 7.4079e-12
18 | 1 | 1 | b4837_A | b4837_B | b4837_C | b18829_A | b18829_B | b18829_C | 0.05428 | 0.09398 | 0.01373 | 0.03151 | 6.2505e-12 | 7.4079e-12
19 | 1 | 1 | b18829_A | b18829_B | b18829_C | b18858_A | b18858_B | b18858_C | 1.333 | 1.5021 | 0.71377 | 0.58678 | 6.2505e-12 | 7.4079e-12
20 | 1 | 1 | 6022828946_A | 6022828946_B | 6022828946_C | b18941_A | b18941_B | b18941_C | 0.1008 | 0.0695 | 0.05825 | 0.02402 | 6.2505e-12 | 7.4079e-12
21 | 1 | 1 | b18941_A | b18941_B | b18941_C | b18948_A | b18948_B | b18948_C | 0.3095 | 0.2852 | 0.23474 | 0.11777 | 6.2505e-12 | 7.4079e-12
22 | 1 | 1 | b18948_A | b18948_B | b18948_C | b18967_A | b18967_B | b18967_C | 0.8703 | 0.8546 | 0.65279 | 0.33845 | 6.2505e-12 | 7.4079e-12
24 | 1 | 1 | b4808_A | b4808_B | b4808_C | b19042_A | b19042_B | b19042_C | 0.58595 | 0.7358 | 0.40688 | 0.2346 | 6.2505e-12 | 7.4079e-12
25 | 1 | 1 | b4760_A | b4760_B | b4760_C | b19052_A | b19052_B | b19052_C | 0.96222 | 1.1823 | 0.66847 | 0.38052 | 6.2505e-12 | 7.4079e-12
26 | 1 | 1 | b4760_A | b4760_B | b4760_C | b19183_A | b19183_B | b19183_C | 0.05599 | 0.17393 | 0.01965 | 0.05722 | 6.2505e-12 | 7.4079e-12
28 | 1 | 1 | b4837_A | b4837_B | b4837_C | b23208_A | b23208_B | b23208_C | 1.0821 | 1.0706 | 0.70762 | 0.35589 | 6.2505e-12 | 7.4079e-12
29 | 1 | 1 | b5213_A | b5213_B | b5213_C | b23283_A | b23283_B | b23283_C | 0.61492 | 1.3527 | 0.22388 | 0.44063 | 6.2505e-12 | 7.4079e-12
3 | 1 | 1 | b4833_A | b4833_B | b4833_C | 5865228330a_A | 5865228330a_B | 5865228330a_C | 0.19871 | 0.1698 | 0.12398 | 0.07856 | 6.2505e-12 | 7.4079e-12
33 | 1 | 1 | b23283_A | b23283_B | b23283_C | b2630_A | b2630_B | b2630_C | 0.30313 | 1.1119 | 0.10962 | 0.34618 | 6.2505e-12 | 7.4079e-12
4 | 1 | 1 | b23208_A | b23208_B | b23208_C | 5890628219_A | 5890628219_B | 5890628219_C | 0.25944 | 0.38941 | 0.15661 | 0.14118 | 6.2505e-12 | 7.4079e-12
40 | 1 | 1 | b4588_A | b4588_B | b4588_C | b4541_A | b4541_B | b4541_C | 1.5662 | 2.5609 | 0.9242 | 0.79857 | 6.2505e-12 | 7.4079e-12
41 | 1 | 1 | b4602_A | b4602_B | b4602_C | b4588_A | b4588_B | b4588_C | 0.38659 | 0.66387 | 0.2174 | 0.20714 | 6.2505e-12 | 7.4079e-12
42 | 1 | 1 | b4725_A | b4725_B | b4725_C | b4602_A | b4602_B | b4602_C | 0.16398 | 0.45992 | 0.04289 | 0.13224 | 6.2505e-12 | 7.4079e-12
43 | 1 | 1 | b4602_A | b4602_B | b4602_C | b4619_A | b4619_B | b4619_C | 0.56131 | 0.81533 | 0.36815 | 0.26046 | 6.2505e-12 | 7.4079e-12
44 | 1 | 1 | b18829_A | b18829_B | b18829_C | b46703_A | b46703_B | b46703_C | 0.34384 | 0.43356 | 0.24301 | 0.13951 | 6.2505e-12 | 7.4079e-12
45 | 1 | 1 | b13649_A | b13649_B | b13649_C | b4725_A | b4725_B | b4725_C | 0.04746 | 0.13262 | 0.01333 | 0.04006 | 6.2505e-12 | 7.4079e-12
46 | 1 | 1 | b4808_A | b4808_B | b4808_C | b4760_A | b4760_B | b4760_C | 0.20572 | 0.60114 | 0.07172 | 0.20177 | 6.2505e-12 | 7.4079e-12
47 | 1 | 1 | b4808_A | b4808_B | b4808_C | b47668_A | b47668_B | b47668_C | 1.0449 | 1.3172 | 0.73226 | 0.42302 | 6.2505e-12 | 7.4079e-12
49 | 1 | 1 | b23208_A | b23208_B | b23208_C | b47983_A | b47983_B | b47983_C | 0.17435 | 0.1963 | 0.11756 | 0.06383 | 6.2505e-12 | 7.4079e-12
50 | 1 | 1 | b4808_A | b4808_B | b4808_C | b4829_A | b4829_B | b4829_C | 0.4942 | 0.54707 | 0.11672 | 0.20892 | 6.2505e-12 | 7.4079e-12
51 | 1 | 1 | b4829_A | b4829_B | b4829_C | b4832_A | b4832_B | b4832_C | 0.10053 | 0.10769 | 0.02455 | 0.04406 | 6.2505e-12 | 7.4079e-12
52 | 1 | 1 | b4832_A | b4832_B | b4832_C | b4833_A | b4833_B | b4833_C | 0.02944 | 0.03288 | 0.00716 | 0.01311 | 6.2505e-12 | 7.4079e-12
53 | 1 | 1 | b18821_A | b18821_B | b18821_C | b4837_A | b4837_B | b4837_C | 0.02401 | 0.03045 | 0.00575 | 0.01124 | 6.2505e-12 | 7.4079e-12
54 | 1 | 1 | b4862_A | b4862_B | b4862_C | b4808_A | b4808_B | b4808_C | 0.10441 | 0.09634 | 0.02848 | 0.04473 | 6.2505e-12 | 7.4079e-12
55 | 1 | 1 | b4877_A | b4877_B | b4877_C | b4862_A | b4862_B | b4862_C | 0.3557 | 0.43083 | 0.12726 | 0.21042 | 6.2505e-12 | 7.4079e-12
56 | 1 | 1 | b4888_A | b4888_B | b4888_C | b4877_A | b4877_B | b4877_C | 0.22838 | 0.23031 | 0.05956 | 0.09408 | 6.2505e-12 | 7.4079e-12
57 | 1 | 1 | b4909_A | b4909_B | b4909_C | b4888_A | b4888_B | b4888_C | 0.47178 | 0.50951 | 0.12584 | 0.20309 | 6.2505e-12 | 7.4079e-12
58 | 1 | 1 | b23283_A | b23283_B | b23283_C | b4909_A | b4909_B | b4909_C | 1.8295 | 2.6391 | 0.52262 | 0.92222 | 6.2505e-12 | 7.4079e-12
59 | 1 | 1 | b23208_A | b23208_B | b23208_C | b51854_A | b51854_B | b51854_C | 0.34315 | 0.38748 | 0.2312 | 0.12578 | 6.2505e-12 | 7.4079e-12
60 | 1 | 1 | b5220_A | b5220_B | b5220_C | b5213_A | b5213_B | b5213_C | 0.10968 | 0.31426 | 0.04895 | 0.10193 | 6.2505e-12 | 7.4079e-12
61 | 1 | 1 | feederhead_A | feederhead_B | feederhead_C | b5220_A | b5220_B | b5220_C | 0.02217 | 0.05959 | 0.00876 | 0.01862 | 6.2505e-12 | 7.4079e-12
63 | 1 | 1 | b4833_A | b4833_B | b4833_C | b56591_A | b56591_B | b56591_C | 0.30444 | 0.37679 | 0.21159 | 0.12085 | 6.2505e-12 | 7.4079e-12
69 | 1 | 1 | b18821_A | b18821_B | b18821_C | b61161_A | b61161_B | b61161_C | 0.15888 | 0.19962 | 0.11037 | 0.06366 | 6.2505e-12 | 7.4079e-12
70 | 1 | 1 | b18821_A | b18821_B | b18821_C | b61423_A | b61423_B | b61423_C | 0.02625 | 0.03322 | 0.01822 | 0.01056 | 6.2505e-12 | 7.4079e-12
End of Three-Phase Line with Sequential Data

## Transformer
Positive-Sequence 2W Transformer
ID | Status | From bus | To bus | R (pu) | Xl (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Phase Shift (deg)
End of Positive-Sequence 2W Transformer
Positive-Sequence 3W Transformer
ID | Status | Bus1 | Bus2 | Bus3 | R_12 (pu) | Xl_12 (pu) | R_23 (pu) | Xl_23 (pu) | R_31 (pu) | Xl_31 (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Ratio W3 (pu) | Phase Shift W1 (deg) | Phase Shift W2 (deg) | Phase Shift W3 (deg)
End of Positive-Sequence 3W Transformer
Multiphase 2W Transformer
ID | Status | Number of phases | Bus1_A | Bus1_B | Bus1_C | V1 (kV) | S_base1 (kVA) | Conn. type1 | Bus2_A | Bus2_B | Bus2_C | V2 (kV) | S_base2 (kVA) | Conn. type2 | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | X (pu) | RW1 (pu) | RW2 (pu)
pv1 | 1 | 3 | b51854_A | b51854_B | b51854_C | 12.47 | 300 | wye | pv1_A | pv1_B | pv1_C | 0.416 | 300 | wye | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0575 | 0.002 | 0.002
pv2 | 1 | 3 | 5865228330a_A | 5865228330a_B | 5865228330a_C | 12.47 | 250 | wye | pv2_A | pv2_B | pv2_C | 0.416 | 250 | wye | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0575 | 0.002 | 0.002
pv3 | 1 | 3 | 5890628219_A | 5890628219_B | 5890628219_C | 12.47 | 1000 | wye | pv3_A | pv3_B | pv3_C | 0.416 | 1000 | wye | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0575 | 0.002 | 0.002
pv4 | 1 | 3 | b4832_A | b4832_B | b4832_C | 12.47 | 500 | wye | pv4_A | pv4_B | pv4_C | 0.416 | 500 | wye | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0575 | 0.002 | 0.002
subxfmr | 1 | 3 | s_A | s_B | s_C | 68.8 | 16000 | wye | ls_bus_A | ls_bus_B | ls_bus_C | 13.09 | 16000 | wye | 1 | 1 | 1 | -8 | 8 | 10 | 10 | 0.1163 | 0.00596 | 0.00596
End of Multiphase 2W Transformer
Multiphase 2W Transformer with Mutual Impedance
ID | Status | Number of phases | Bus1_A | Bus1_B | Bus1_C | V1 (kV) | S_base1 (kVA) | Conn. type1 | Bus2_A | Bus2_B | Bus2_C | V2 (kV) | S_base2 (kVA) | Conn. type2 | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | Z0 leakage (pu) | Z1 leakage (pu) | X0/R0 | X1/R1 | No Load Loss (kW)
End of Multiphase 2W Transformer with Mutual Impedance

## Bus
Bus | Base Voltage (V) | Initial Vmag | Unit (V, pu) | Angle (deg) | Type
5848128103_C | 7199.5579 | 1 | pu | 120 | PQ
5851228580_C | 7199.5579 | 1 | pu | 120 | PQ
5865228330a_A | 7199.5579 | 1 | pu | 0 | PQ
5865228330a_C | 7199.5579 | 1 | pu | 120 | PQ
5865228330a_B | 7199.5579 | 1 | pu | -120 | PQ
5890628219_A | 7199.5579 | 1 | pu | 0 | PQ
5890628219_C | 7199.5579 | 1 | pu | 120 | PQ
5890628219_B | 7199.5579 | 1 | pu | -120 | PQ
5912527743_A | 7199.5579 | 1 | pu | 0 | PQ
5925528209a_C | 7199.5579 | 1 | pu | 120 | PQ
5962929303_B | 7199.5579 | 1 | pu | -120 | PQ
5967328881_B | 7199.5579 | 1 | pu | -120 | PQ
5988528387_C | 7199.5579 | 1 | pu | 120 | PQ
5998528541_C | 7199.5579 | 1 | pu | 120 | PQ
6022828946_A | 7199.5579 | 1 | pu | 0 | PQ
6022828946_C | 7199.5579 | 1 | pu | 120 | PQ
6022828946_B | 7199.5579 | 1 | pu | -120 | PQ
6093229888_A | 7199.5579 | 1 | pu | 0 | PQ
b13649_A | 7199.5579 | 1 | pu | 0 | PQ
b13649_C | 7199.5579 | 1 | pu | 120 | PQ
b13649_B | 7199.5579 | 1 | pu | -120 | PQ
b13923_C | 7199.5579 | 1 | pu | 120 | PQ
b14440_C | 7199.5579 | 1 | pu | 120 | PQ
b17991_C | 7199.5579 | 1 | pu | 120 | PQ
b18821_A | 7199.5579 | 1 | pu | 0 | PQ
b18821_C | 7199.5579 | 1 | pu | 120 | PQ
b18821_B | 7199.5579 | 1 | pu | -120 | PQ
b18829_A | 7199.5579 | 1 | pu | 0 | PQ
b18829_C | 7199.5579 | 1 | pu | 120 | PQ
b18829_B | 7199.5579 | 1 | pu | -120 | PQ
b18858_A | 7199.5579 | 1 | pu | 0 | PQ
b18858_C | 7199.5579 | 1 | pu | 120 | PQ
b18858_B | 7199.5579 | 1 | pu | -120 | PQ
b18941_A | 7199.5579 | 1 | pu | 0 | PQ
b18941_C | 7199.5579 | 1 | pu | 120 | PQ
b18941_B | 7199.5579 | 1 | pu | -120 | PQ
b18948_C | 7199.5579 | 1 | pu | 120 | PQ
b18948_A | 7199.5579 | 1 | pu | 0 | PQ
b18948_B | 7199.5579 | 1 | pu | -120 | PQ
b18967_A | 7199.5579 | 1 | pu | 0 | PQ
b18967_C | 7199.5579 | 1 | pu | 120 | PQ
b18967_B | 7199.5579 | 1 | pu | -120 | PQ
b19028_A | 7199.5579 | 1 | pu | 0 | PQ
b19028_B | 7199.5579 | 1 | pu | -120 | PQ
b19042_A | 7199.5579 | 1 | pu | 0 | PQ
b19042_C | 7199.5579 | 1 | pu | 120 | PQ
b19042_B | 7199.5579 | 1 | pu | -120 | PQ
b19052_A | 7199.5579 | 1 | pu | 0 | PQ
b19052_C | 7199.5579 | 1 | pu | 120 | PQ
b19052_B | 7199.5579 | 1 | pu | -120 | PQ
b19183_A | 7199.5579 | 1 | pu | 0 | PQ
b19183_C | 7199.5579 | 1 | pu | 120 | PQ
b19183_B | 7199.5579 | 1 | pu | -120 | PQ
b22803_C | 7199.5579 | 1 | pu | 120 | PQ
b23208_A | 7199.5579 | 1 | pu | 0 | PQ
b23208_C | 7199.5579 | 1 | pu | 120 | PQ
b23208_B | 7199.5579 | 1 | pu | -120 | PQ
b23283_A | 7199.5579 | 1 | pu | 0 | PQ
b23283_C | 7199.5579 | 1 | pu | 120 | PQ
b23283_B | 7199.5579 | 1 | pu | -120 | PQ
b23416_A | 7199.5579 | 1 | pu | 0 | PQ
b24288_C | 7199.5579 | 1 | pu | 120 | PQ
b24504_C | 7199.5579 | 1 | pu | 120 | PQ
b2630_A | 7199.5579 | 1 | pu | 0 | PQ
b2630_C | 7199.5579 | 1 | pu | 120 | PQ
b2630_B | 7199.5579 | 1 | pu | -120 | PQ
b29921_C | 7199.5579 | 1 | pu | 120 | PQ
b31997_C | 7199.5579 | 1 | pu | 120 | PQ
b32783_B | 7199.5579 | 1 | pu | -120 | PQ
b35443_C | 7199.5579 | 1 | pu | 120 | PQ
b41878_A | 7199.5579 | 1 | pu | 0 | PQ
b41878_B | 7199.5579 | 1 | pu | -120 | PQ
b43438_A | 7199.5579 | 1 | pu | 0 | PQ
b43438_B | 7199.5579 | 1 | pu | -120 | PQ
b4541_A | 7199.5579 | 1 | pu | 0 | PQ
b4541_C | 7199.5579 | 1 | pu | 120 | PQ
b4541_B | 7199.5579 | 1 | pu | -120 | PQ
b4588_A | 7199.5579 | 1 | pu | 0 | PQ
b4588_C | 7199.5579 | 1 | pu | 120 | PQ
b4588_B | 7199.5579 | 1 | pu | -120 | PQ
b4602_A | 7199.5579 | 1 | pu | 0 | PQ
b4602_C | 7199.5579 | 1 | pu | 120 | PQ
b4602_B | 7199.5579 | 1 | pu | -120 | PQ
b4619_A | 7199.5579 | 1 | pu | 0 | PQ
b4619_C | 7199.5579 | 1 | pu | 120 | PQ
b4619_B | 7199.5579 | 1 | pu | -120 | PQ
b46703_A | 7199.5579 | 1 | pu | 0 | PQ
b46703_C | 7199.5579 | 1 | pu | 120 | PQ
b46703_B | 7199.5579 | 1 | pu | -120 | PQ
b4725_C | 7199.5579 | 1 | pu | 120 | PQ
b4725_A | 7199.5579 | 1 | pu | 0 | PQ
b4725_B | 7199.5579 | 1 | pu | -120 | PQ
b4760_A | 7199.5579 | 1 | pu | 0 | PQ
b4760_C | 7199.5579 | 1 | pu | 120 | PQ
b4760_B | 7199.5579 | 1 | pu | -120 | PQ
b47668_A | 7199.5579 | 1 | pu | 0 | PQ
b47668_C | 7199.5579 | 1 | pu | 120 | PQ
b47668_B | 7199.5579 | 1 | pu | -120 | PQ
b47846_C | 7199.5579 | 1 | pu | 120 | PQ
b47983_C | 7199.5579 | 1 | pu | 120 | PQ
b47983_A | 7199.5579 | 1 | pu | 0 | PQ
b47983_B | 7199.5579 | 1 | pu | -120 | PQ
b4808_A | 7199.5579 | 1 | pu | 0 | PQ
b4808_C | 7199.5579 | 1 | pu | 120 | PQ
b4808_B | 7199.5579 | 1 | pu | -120 | PQ
b4829_A | 7199.5579 | 1 | pu | 0 | PQ
b4829_C | 7199.5579 | 1 | pu | 120 | PQ
b4829_B | 7199.5579 | 1 | pu | -120 | PQ
b4832_A | 7199.5579 | 1 | pu | 0 | PQ
b4832_C | 7199.5579 | 1 | pu | 120 | PQ
b4832_B | 7199.5579 | 1 | pu | -120 | PQ
b4833_A | 7199.5579 | 1 | pu | 0 | PQ
b4833_C | 7199.5579 | 1 | pu | 120 | PQ
b4833_B | 7199.5579 | 1 | pu | -120 | PQ
b4837_A | 7199.5579 | 1 | pu | 0 | PQ
b4837_C | 7199.5579 | 1 | pu | 120 | PQ
b4837_B | 7199.5579 | 1 | pu | -120 | PQ
b4862_A | 7199.5579 | 1 | pu | 0 | PQ
b4862_C | 7199.5579 | 1 | pu | 120 | PQ
b4862_B | 7199.5579 | 1 | pu | -120 | PQ
b4877_A | 7199.5579 | 1 | pu | 0 | PQ
b4877_C | 7199.5579 | 1 | pu | 120 | PQ
b4877_B | 7199.5579 | 1 | pu | -120 | PQ
b4888_A | 7199.5579 | 1 | pu | 0 | PQ
b4888_C | 7199.5579 | 1 | pu | 120 | PQ
b4888_B | 7199.5579 | 1 | pu | -120 | PQ
b4909_A | 7199.5579 | 1 | pu | 0 | PQ
b4909_C | 7199.5579 | 1 | pu | 120 | PQ
b4909_B | 7199.5579 | 1 | pu | -120 | PQ
b51854_A | 7199.5579 | 1 | pu | 0 | PQ
b51854_C | 7199.5579 | 1 | pu | 120 | PQ
b51854_B | 7199.5579 | 1 | pu | -120 | PQ
b5213_A | 7199.5579 | 1 | pu | 0 | PQ
b5213_C | 7199.5579 | 1 | pu | 120 | PQ
b5213_B | 7199.5579 | 1 | pu | -120 | PQ
b5220_A | 7199.5579 | 1 | pu | 0 | PQ
b5220_C | 7199.5579 | 1 | pu | 120 | PQ
b5220_B | 7199.5579 | 1 | pu | -120 | PQ
b52275_C | 7199.5579 | 1 | pu | 120 | PQ
b56591_A | 7199.5579 | 1 | pu | 0 | PQ
b56591_C | 7199.5579 | 1 | pu | 120 | PQ
b56591_B | 7199.5579 | 1 | pu | -120 | PQ
b56685_B | 7199.5579 | 1 | pu | -120 | PQ
b57691_A | 7199.5579 | 1 | pu | 0 | PQ
b58809_C | 7199.5579 | 1 | pu | 120 | PQ
b59935_A | 7199.5579 | 1 | pu | 0 | PQ
b60868_C | 7199.5579 | 1 | pu | 120 | PQ
b61161_A | 7199.5579 | 1 | pu | 0 | PQ
b61161_C | 7199.5579 | 1 | pu | 120 | PQ
b61161_B | 7199.5579 | 1 | pu | -120 | PQ
b61423_A | 7199.5579 | 1 | pu | 0 | PQ
b61423_C | 7199.5579 | 1 | pu | 120 | PQ
b61423_B | 7199.5579 | 1 | pu | -120 | PQ
b63378_C | 7199.5579 | 1 | pu | 120 | PQ
fdr_bus_A | 7199.5579 | 1 | pu | 0 | PQ
fdr_bus_C | 7199.5579 | 1 | pu | 120 | PQ
fdr_bus_B | 7199.5579 | 1 | pu | -120 | PQ
feederhead_A | 7199.5579 | 1 | pu | 0 | PQ
feederhead_C | 7199.5579 | 1 | pu | 120 | PQ
feederhead_B | 7199.5579 | 1 | pu | -120 | PQ
g36748_A | 7199.5579 | 1 | pu | 0 | PQ
g42394_C | 7199.5579 | 1 | pu | 120 | PQ
ls_bus_A | 7199.5579 | 1 | pu | 0 | PQ
ls_bus_C | 7199.5579 | 1 | pu | 120 | PQ
ls_bus_B | 7199.5579 | 1 | pu | -120 | PQ
pv1_A | 240.1777 | 1 | pu | 0 | PQ
pv1_C | 240.1777 | 1 | pu | 120 | PQ
pv1_B | 240.1777 | 1 | pu | -120 | PQ
pv2_A | 240.1777 | 1 | pu | 0 | PQ
pv2_C | 240.1777 | 1 | pu | 120 | PQ
pv2_B | 240.1777 | 1 | pu | -120 | PQ
pv3_A | 240.1777 | 1 | pu | 0 | PQ
pv3_C | 240.1777 | 1 | pu | 120 | PQ
pv3_B | 240.1777 | 1 | pu | -120 | PQ
pv4_A | 240.1777 | 1 | pu | 0 | PQ
pv4_C | 240.1777 | 1 | pu | 120 | PQ
pv4_B | 240.1777 | 1 | pu | -120 | PQ
s_A | 39837.1686 | 1 | pu | 0 | SLACK
s_C | 39837.1686 | 1 | pu | 120 | SLACK
s_B | 39837.1686 | 1 | pu | -120 | SLACK

## Switch
From Bus | To Bus | ID | Status
fdr_bus_A | feederhead_A | feeder_A | 1
fdr_bus_B | feederhead_B | feeder_B | 1
fdr_bus_C | feederhead_C | feeder_C | 1
ls_bus_A | fdr_bus_A | temp_sub_A | 1
ls_bus_B | fdr_bus_B | temp_sub_B | 1
ls_bus_C | fdr_bus_C | temp_sub_C | 1