## General
Excel file version | v2.0
Name | acep_psil
Frequency (Hz) | 60
Power Base (MVA) | 100

## Voltage Source
Type
PositiveSeqVsource
SinglePhaseVsource
ThreePhaseShortCircuitVsource
ThreePhaseSequentialVsource
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive Sequence Voltage Source |  |  |  | Go to Type List
ID | Bus | Voltage (pu) | Angle (deg) | Rs (pu) | Xs (pu)
End of Positive Sequence Voltage Source
Single-Phase Voltage Source |  |  |  | Go to Type List
ID | Bus1 | Voltage (V) | Angle (deg) | Rs (Ohm) | Xs (Ohm)
End of Single-Phase Voltage Source
Three-Phase Voltage Source with Short-Circuit Level Data |  |  |  | Go to Type List
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | SC1ph (MVA) | SC3ph (MVA)
End of Three-Phase Voltage Source with Short-Circuit Level Data
Three-Phase Voltage Source with Sequential Data |  |  |  | Go to Type List
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | R1 (Ohm) | X1 (Ohm) | R0 (Ohm) | X0 (Ohm)
VS_source | gen1_A | gen1_B | gen1_C | 0.5472 | 0 | 0.006 | 0.06 | 0.006 | 0.06
End of Three-Phase Voltage Source with Sequential Data

## Load
Type
PositiveSeqZload | ThreePhaseZIPLoad
PositiveSeqPload
PositiveSeqIload
SinglePhaseZIPLoad
TwoPhaseZIPLoad
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Constant Imepedance Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Constant Imepedance Load
Positive-Sequence Constant Power Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Constant Power Load
Positive-Sequence Constant Current Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Constant Current Load
Single-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | P1 (kW) | Q1 (kVAr)
End of SinglePhase ZIP Load
Two-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr)
End of TwoPhase ZIP Load
Three-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | Bus3 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
LD_load208 | 1 | 0.208 | 0.12 | wye | 0 | 0 | 100 | 0 | bank1_A | bank1_B | bank1_C | 83.4667 | 62.6 | 83.4667 | 62.6 | 83.4667 | 62.6
LD_load480 | 1 | 0.48 | 0.12 | wye | 0 | 0 | 100 | 0 | load2_A | load2_B | load2_C | 83.4667 | 62.6 | 83.4667 | 62.6 | 83.4667 | 62.6
LD_pv_solar | 1 | 0.48 | 0.12 | wye | 0 | 100 | 0 | 0 | solar_A | solar_B | solar_C | -8.3333 | 0 | -8.3333 | 0 | -8.3333 | 0
LD_bat_leadacid | 1 | 0.318 | 0.12 | wye | 0 | 100 | 0 | 0 | battinv_A | battinv_B | battinv_C | -33.3333 | 0 | -33.3333 | 0 | -33.3333 | 0
End of ThreePhase ZIP Load

## Shunt
Type
PositiveSeqShunt
SinglePhaseShunt
TwoPhaseShunt
ThreePhaseShunt
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive Sequence Shunt |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive Sequence Shunt
Single-Phase Shunt |  | Go to Type List
ID | Status | kV (ph-gr RMS) | Bus1 | P1 (kW) | Q1 (kVAr)
End of Single-Phase Shunt
Two-Phase Shunt |  | Go to Type List
ID | Status1 | Status2 | kV (ph-gr RMS) | Bus1 | Bus2 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr)
End of Two-Phase Shunt
Three-Phase Shunt |  | Go to Type List
ID | Status1 | Status2 | Status3 | kV (ph-gr RMS) | Bus1 | Bus2 | Bus3 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
End of Three-Phase Shunt

## Line
Type
PositiveSeqLine
SinglePhaseLine
TwoPhaseLine
ThreePhaseLineFullData
ThreePhaseLineSequentialData
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Line |  | Go to Type List
ID | Status | From bus | To bus | R (pu) | X (pu) | B (pu)
End of Positive-Sequence Line
Single-Phase Line |  | Go to Type List
ID | Status | Length | From1 | To1 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | b11 (uS/length_unit)
End of Single-Phase Line
Two-Phase Line |  | Go to Type List
ID | Status | Length | From1 | From2 | To1 | To2 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit)
End of Two-Phase Line
Three-Phase Line with Full Data |  | Go to Type List
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | r31 (Ohm/length_unit) | x31 (Ohm/length_unit) | r32 (Ohm/length_unit) | x32 (Ohm/length_unit) | r33 (Ohm/length_unit) | x33 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit) | b31 (uS/length_unit) | b32 (uS/length_unit) | b33 (uS/length_unit)
End of Three-Phase Line with Full Data
Three-Phase Line with Sequential Data |  | Go to Type List
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | R0 (Ohm/length_unit) | X0 (Ohm/length_unit) | R1 (Ohm/length_unit) | X1 (Ohm/length_unit) | B0 (uS/length_unit) | B1 (uS/length_unit)
LN_seg1 | 1 | 3.81 | gen1_A | gen1_B | gen1_C | wind_A | wind_B | wind_C | 0.00012427 | 0.00037282 | 1.2427e-05 | 0.0004971 | 0 | 0
LN_seg2 | 1 | 11.43 | wind_A | wind_B | wind_C | load1_A | load1_B | load1_C | 0.00012427 | 0.00037282 | 1.2427e-05 | 0.0004971 | 0 | 0
LN_seg3 | 1 | 7.62 | load1_A | load1_B | load1_C | batt_A | batt_B | batt_C | 0.00012427 | 0.00037282 | 1.2427e-05 | 0.0004971 | 0 | 0
LN_seg4 | 1 | 7.62 | batt_A | batt_B | batt_C | solar_A | solar_B | solar_C | 0.00012427 | 0.00037282 | 1.2427e-05 | 0.0004971 | 0 | 0
LN_seg5 | 1 | 7.62 | solar_A | solar_B | solar_C | load2_A | load2_B | load2_C | 0.00012427 | 0.00037282 | 1.2427e-05 | 0.0004971 | 0 | 0
End of Three-Phase Line with Sequential Data

## Transformer
Type
PositiveSeq2wXF
PositiveSeq3wXF
Multiphase2wXF
Multiphase2wXFMutual
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence 2W Transformer |  |  | Go to Type List
ID | Status | From bus | To bus | R (pu) | Xl (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Phase Shift (deg)
End of Positive-Sequence 2W Transformer
Positive-Sequence 3W Transformer |  |  | Go to Type List
ID | Status | Bus1 | Bus2 | Bus3 | R_12 (pu) | Xl_12 (pu) | R_23 (pu) | Xl_23 (pu) | R_31 (pu) | Xl_31 (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Ratio W3 (pu) | Phase Shift W1 (deg) | Phase Shift W2 (deg) | Phase Shift W3 (deg)
End of Positive-Sequence 3W Transformer
Multiphase 2W Transformer |  |  | Go to Type List
ID | Status | Number of phases | Bus1_A | Bus1_B | Bus1_C | V1 (kV) | S_base1 (kVA) | Conn. type1 | Bus2_A | Bus2_B | Bus2_C | V2 (kV) | S_base2 (kVA) | Conn. type2 | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | X (pu) | RW1 (pu) | RW2 (pu)
End of Multiphase 2W Transformer
Multiphase 2W Transformer with Mutual Impedance |  |  | Go to Type List
ID | Status | Number of phases | Bus1_A | Bus1_B | Bus1_C | V1 (kV) | S_base1 (kVA) | Conn. type1 | Bus2_A | Bus2_B | Bus2_C | V2 (kV) | S_base2 (kVA) | Conn. type2 | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | Z0 leakage (pu) | Z1 leakage (pu) | X0/R0 | X1/R1 | No Load Loss (kW)
XF_batt | 1 | 3 | batt_A | batt_B | batt_C | 0.48 | 313 | wye | battinv_A | battinv_B | battinv_C | 0.318 | 313 | delta | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058054 | 0.058054 | 7.1875 | 7.1875 | 0.626
XF_load1 | 1 | 3 | load1_A | load1_B | load1_C | 0.48 | 300 | delta | bank1_A | bank1_B | bank1_C | 0.208 | 300 | wye | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058054 | 0.058054 | 7.1875 | 7.1875 | 0.6
End of Multiphase 2W Transformer with Mutual Impedance

## Machine
Type
SyncGenGENCLS | AsyncGenSingleCage
SyncGenGENROE | AsyncGenDoubleCage
SyncGenGENROU
SyncGenGENSAE
SyncGenGENSAL
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
SyncGenGENCLS | Go to Type List
Bus | ID | Status | Pg (MW) | Qg (MVAr) | Qmin (MVAr) | Qmax (MVAr) | Sbase (MVA) | H (s) | D | Ra (pu) | x'_d (pu)
wind | SM_wind | 1 | 0.1 | 0.053974 | -0.053974 | 0.053974 | 0.12 | 3 | 0.001 | 0.01 | 0.5
End of SyncGenGENCLS
SyncGenGENROE | Go to Type List
Bus | ID | Status | Pg (MW) | Qg (MVAr) | Qmin (MVAr) | Qmax (MVAr) | Sbase (MVA) | H (s) | D | Ra (pu) | x_d (pu) | x_q (pu) | x'_d (pu) | x'_q (pu) | x''_d (pu) | x_l (pu) | T'_do (s) | T''_do (s) | T'_qo (s) | T''_qo (s) | S10 | S12
End of SyncGenGENROE
SyncGenGENROU | Go to Type List
Bus | ID | Status | Pg (MW) | Qg (MVAr) | Qmin (MVAr) | Qmax (MVAr) | Sbase (MVA) | H (s) | D | Ra (pu) | x_d (pu) | x_q (pu) | x'_d (pu) | x'_q (pu) | x''_d (pu) | x_l (pu) | T'_do (s) | T''_do (s) | T'_qo (s) | T''_qo (s) | S10 | S12
End of SyncGenGENROU
SyncGenGENSAE | Go to Type List
Bus | ID | Status | Pg (MW) | Qg (MVAr) | Qmin (MVAr) | Qmax (MVAr) | Sbase (MVA) | H (s) | D | Ra (pu) | x_d (pu) | x_q (pu) | x'_d (pu) | x''_d (pu) | x_l (pu) | T'_do (s) | T''_do (s) | T''_qo (s) | S10 | S12
End of SyncGenGENSAE
SyncGenGENSAL | Go to Type List
Bus | ID | Status | Pg (MW) | Qg (MVAr) | Qmin (MVAr) | Qmax (MVAr) | Sbase (MVA) | H (s) | D | Ra (pu) | x_d (pu) | x_q (pu) | x'_d (pu) | x''_d (pu) | x_l (pu) | T'_do (s) | T''_do (s) | T''_qo (s) | S10 | S12
End of SyncGenGENSAL
AsyncGenSingleCage | Go to Type List
Bus | ID | Status | Pg (MW) | Qg (MVAr) | Qmin (MVAr) | Qmax (MVAr) | Sbase (MVA) | Pmech0 (pu) | H (s) | Ra (pu) | x (pu) | x' (pu) | x_l (pu) | T' (s) | e1 (pu) | e2 (pu) | S(e1) | S(e2)
End of AsyncGenSingleCage
AsyncGenDoubleCage | Go to Type List
Bus | ID | Status | Pg (MW) | Qg (MVAr) | Qmin (MVAr) | Qmax (MVAr) | Sbase (MVA) | Pmech0 (pu) | H (s) | Ra (pu) | x (pu) | x' (pu) | x'' (pu) | x_l (pu) | T' (s) | T'' (s) | e1 (pu) | e2 (pu) | S(e1) | S(e2)
End of AsyncGenDoubleCage

## Bus
Bus | Base Voltage (V) | Initial Vmag | Unit (V, pu) | Angle (deg) | Type
bank1_A | 120.0889 | 1 | pu | 0 | PQ
bank1_B | 120.0889 | 1 | pu | -120 | PQ
bank1_C | 120.0889 | 1 | pu | 120 | PQ
batt_A | 277.1281 | 1 | pu | 0 | PQ
batt_B | 277.1281 | 1 | pu | -120 | PQ
batt_C | 277.1281 | 1 | pu | 120 | PQ
battinv_A | 183.5974 | 1 | pu | 0 | PQ
battinv_B | 183.5974 | 1 | pu | -120 | PQ
battinv_C | 183.5974 | 1 | pu | 120 | PQ
gen1_A | 277.1281 | 1 | pu | 0 | SLACK
gen1_B | 277.1281 | 1 | pu | -120 | SLACK
gen1_C | 277.1281 | 1 | pu | 120 | SLACK
load1_A | 277.1281 | 1 | pu | 0 | PQ
load1_B | 277.1281 | 1 | pu | -120 | PQ
load1_C | 277.1281 | 1 | pu | 120 | PQ
load2_A | 277.1281 | 1 | pu | 0 | PQ
load2_B | 277.1281 | 1 | pu | -120 | PQ
load2_C | 277.1281 | 1 | pu | 120 | PQ
solar_A | 277.1281 | 1 | pu | 0 | PQ
solar_B | 277.1281 | 1 | pu | -120 | PQ
solar_C | 277.1281 | 1 | pu | 120 | PQ
wind_A | 277.1281 | 1 | pu | 0 | PQ
wind_B | 277.1281 | 1 | pu | -120 | PQ
wind_C | 277.1281 | 1 | pu | 120 | PQ

## Switch
From Bus | To Bus | ID | Status