## DER_A-rev1 PVMOD
Name | Datatype | Default | Description | Reference: This model is based on [3] with extensions for "continued dynamic voltage support following abnormal voltages (e.g., due to faults) as they have been developed under EPRI's PV-MOD project. Default values represent IEEE 1547-2018 Category II DER
Trv | float | 0.02 | transducer time constant (s) for voltage measurement
Trf | float | n/a | transducer time constant (s) for frequency measurement (must be ≥ 0.02 s)
dbd1 | float | -99 | lower voltage deadband ≤ 0 (pu)
dbd2 | float | 99 | upper voltage deadband ≥ 0 (pu)
Kqv | float | 0 | proportional voltage control gain (pu/pu)
Vref0 | float | 0 | voltage reference set-point > 0 (pu)
Tp | float | 0.02 | transducer time constant (s)
Tiq | float | 0.02 | Q control time constant (s)
Ddn | float | 20 | frequency control droop gain ≥ 0 (down-side)
Dup | float | 20 | frequency control droop gain ≥ 0 (up-side)
fdbd1 | float | -0.0006 | lower frequency control deadband ≤ 0 (pu)
fdbd2 | float | 0.0006 | upper frequency control deadband ≥ 0 (pu)
femax | float | 99 | frequency control maximum error ≥ 0 (pu)
femin | float | -99 | frequency control minimum error ≤ 0 (pu)
Pmax | float | 1 | Maximum power (pu)
Pmin | float | 0 | Minimum power (pu)
dPmax | float | 99 | Power ramp rate up > 0 (pu/s)
dPmin | float | -99 | Power ramp rate down < 0 (pu/s)
Tpord | float | 5 | Power order time constant (s)
Kpg | float | 0.1 | active power control proportional gain
Kig | float | 10 | active power control integral gain
Imax | float | 1.2 | Maximum converter current (pu)
vl0 | float | 0.44 | voltage break-point for low voltage cut-out of inverters
vl1 | float | 0.44+Vdrop | voltage break-point for low voltage cut-out of inverters
vh0 | float | 1.2 | voltage break-point for high voltage cut-out of inverters
vh1 | float | 1.2-Vdrop | voltage break-point for high voltage cut-out of inverters
tvl0 | float | 0.16 | timer for vl0 point
tvl1 | float | 0.16 | timer for vl1 point
tvh0 | float | 0.16 | timer for vh0 point
tvh1 | float | 0.16 | timer for vh1 point
Vrfrac | float | 1 | fraction of device that recovers after voltage comes back to within vl1 < V < vh1
fl | float | n/a | frequency break-point for low frequency cut-out of inverters
fh | float | n/a | frequency break-point for high frequency cut-out of inverters
tfl | float | 300 or 0.16 | timer for fl (Tfl > Trf)
tfh | float | 300 or 0.16 | timer for fh
Tg | float | 0.02 | Current control time constant
rrpwr | float | 2 | Power rise ramp rate following a fault > 0 (pu/s)
Tv | float | 0.02 | time constant on the output of the voltage/frequency cut?out
Vpr | float | 0.3 | voltage below which frequency tripping is disabled
Pflag | enum | 1 | 0 - for constant Q control, and 1 - constant power factor control
Pqflag | enum | 0 | 0 - Q priority, 1 - P priority for current limit
Freq_flag | enum | n/a | 0 - frequency control disabled, and 1 - frequency control enabled
Ftripflag | enum | n/a | 0 - frequency tripping disabled; 1 - frequency tripping enabled
Vtripflag | enum | n/a | 0 - voltage tripping disabled; 1 - voltage tripping enabled
typeflag | enum | 0 or 1 | 0 - the unit is a storage device and Ipmin = -Ipmax; 1 (or any value other than 0) - the unit is a generator Ipmin = 0;
Xe | float | 0.25 | Source impedance reactive > 0 (pu)
Iqh1 | float | 1 | Maximum limit of reactive current injection, p.u.
Iql1 | float | -1 | Minimum limit of reactive current injection, p.u.
Vdip | float | 0.8 | Trigger voltage for dynamic voltage support under abnormal voltage conditions |  | EPRI Enhancements
Kiv | float | 0 | Integral control for dynamic voltage support under abnormal voltage conditions
Tdb | float | 5 | Time to hold dynamic voltage support following abnormal voltage conditions

## DER_IEEE1547-2018_Cat B-III Def
Param_Name | Data_Type | Default | Description | Unit | Value_Options | Reference: See [16] for specifications of columns A, B, D, E, and F. Column C based on IEEE 1547-2018.
NP_P_MAX | Number |  | Active power rating in kilowatts at unity power factor | kW |  | Nameplate Data
NP_P_MAX_OVER_PF | Number |  | Active power rating in kilowatts at specified over-excited power factor | kW
NP_OVER_PF | Number |  | Over-excited power factor
NP_P_MAX_UNDER_PF | Number |  | Active power rating in kilowatts at specified under-excited power factor | kW
NP_UNDER_PF | Number |  | Under-excited power factor
NP_VA_MAX | Number |  | Maximum apparent power rating in kilovolt-amperes | kVA
NP_NORMAL_OP_CAT | Select-list | CAT_B | Normal performance capability |  | CAT_A/CAT_B
NP_ABNORMAL_OP_CAT | Select-list | CAT_III | Abnormal performance Category |  | CAT_I/CAT_II/CAT_III
NP_Q_MAX_INJ | Number |  | Maximum injected reactive power rating in kilovolt-amperes reactive | kVAr
NP_Q_MAX_ABS | Number |  | Maximum absorbed reactive power rating in kilovolt-amperes reactive | kVAr
NP_P_MAX_CHARGE | Number |  | Maximum active power charge rating in kilowatts | kW
NP_APPARENT_POWER_CHARGE_MAX | Number |  | Maximum apparent power charge rating in kilo Volt Amperes. May differ from the apparent power maximum rating. | kVA
NP_AC_V_NOM | Number |  | Voltage Base Nominal AC voltage rating in RMS Vac | Vac
NP_AC_V_MAX | Number |  | AC voltage rating in RMS Volts | Vac
NP_AC_V_MIN | Number |  | AC voltage rating in RMS Volts | Vac
NP_SUPPORTED_MODES | Multi-list |  | Indication of support for each control mode function separated by dashes |  | CONST_PF/CONST_Q/QV/QP/PV/PF
NP_REACTIVE_SUSCEPTANCE | Number |  | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state | Siemens
NP_MANUFACTURER | Text |  | Manufacturer
NP_MODEL | Text |  | Model
NP_SERIAL_NUM | Text |  | Serial number
NP_FW_VER | Text |  | FW Version
AP_LIMIT_P_ENABLE | Select-list | Disabled | Limit active power enable |  | ENABLED/DISABLED | Power Limit Settings
AP_MAX_P | Number | 100 | Maximum active power setting | %
ES_PERMIT_SERVICE | Select-list | Enabled | This function is activated by request from the Area EPS Operator |  | ENABLED/DISABLED | Enter Service Settings
ES_V_LOW | Number | 0.917 | Per unit value based on NP_AC_V_NOM (voltage base). Voltage shall be equal to or greater than default value. | V p.u.
ES_V_HIGH | Number | 1.05 | Per unit value based on NP_AC_V_NOM (voltage base). Voltage shall be equal to or less than default value. | V p.u.
ES_F_LOW | Number | 59.5 | Frequency shall be equal to or greater than default value. Frequency values shall be reported to 3 decimal places. | Hz
ES_F_HIGH | Number | 60.1 | Frequency shall be equal to or less than default value. Frequency values shall be reported to 3 decimal places. | Hz
ES_DELAY | Number | 300 | Minimum intentional delay before initiating Soft-Start | s
ES_RANDOMIZED_DELAY | Number | 300 | Enter service radomized delay is an optional feature in IEEE Std 1547-2018 | s
ES_RAMP_RATE | Number | 300 | Enter service soft-start duration. Time from zero to 100% NP_P_MAX | s
CONST_PF_MODE_ENABLE | Select-list | Enabled | Constant power factor mode select |  | ENABLED/DISABLED | Constant Power Factor Settings
CONST_PF_EXCITATION | Select-list | INJ | Under or over excited |  | INJ/ABS
CONST_PF | Number | 1 | Power factor setting
CONST_Q_MODE_ENABLE | Select-list | Disabled | Constant reactive power mode select |  | ENABLED/DISABLED | Constant Q Settings
CONST_Q | Number | 0 | Injecting reactive power setting. Per unit value based on NP_Q_MAX_INJ. Negative signs should not be used but if present, indicates absorbing VAr based on NP_Q_MAX_ABS. | VAr p.u.
QV_MODE_ENABLE | Select-list | Disabled | ENABLED/DISABLED - specified by AEPSO |  | ENABLED/DISABLED | Volt-Var Settings
QV_VREF | Number | 1 | Per unit value based on NP_AC_V_NOM (voltage base) | V p.u.
QV_VREF_AUTO_MODE | Select-list | Enabled | ENABLED/DISABLED - specified by AEPSO |  | ENABLED/DISABLED
QV_VREF_OLRT | Number | - | Vref time constant in seconds as specified by the area EPS operator | s
QV_CURVE_V2 | Number | 0.98 | Undervoltage magnitude where VArs are at minimum. Per unit value based on NP_AC_V_NOM (voltage base) | V p.u.
QV_CURVE_Q2 | Number | 0 | VArs at V2. Per unit value based on NP_Q_MAX_INJ or NP_Q_MAX_ABS. Negative signs should not be used but if present, indicates absorbing VAr. | VAr p.u.
QV_CURVE_V3 | Number | 1.02 | Overvoltage magnitude where VArs are at minimum. Per unit value based on NP_AC_V_NOM (voltage base) | V p.u.
QV_CURVE_Q3 | Number | 0 | VArs at V3. Per unit value based on NP_Q_MAX_INJ or NP_Q_MAX_ABS. Negative signs should not be used but if present, indicates absorbing VAr. | VAr p.u.
QV_CURVE_V1 | Number | 0.92 | Undervoltage magnitude where VArs are at maximum. Per unit value based on NP_AC_V_NOM (voltage base) | V p.u.
QV_CURVE_Q1 | Number | 0.44 | VArs at V1. Per unit value based on NP_Q_MAX_INJ or NP_Q_MAX_ABS. Negative signs should not be used but if present, indicates absorbing VAr. | VAr p.u.
QV_CURVE_V4 | Number | 1.08 | Overvoltage magnitude where VArs are at minimum. Per unit value based on NP_AC_V_NOM (voltage base) | V p.u.
QV_CURVE_Q4 | Number | -0.44 | VArs at V4. Per unit value based on NP_Q_MAX_INJ or NP_Q_MAX_ABS. Negative signs should not be used but if present, indicates absorbing VAr. | VAr p.u.
QV_OLRT | Number | 5 | Volt-VAr open loop response time | s
QP_MODE_ENABLE | Select-list | Disabled | This function is deactivated by request from the Area EPS Operator |  | ENABLED/DISABLED | Watt-Var Settings
QP_CURVE_P3_GEN | Number | 1 | Maximum active power (generating). Per unit value based on NP_P_MAX. | P p.u.
QP_CURVE_P2_GEN | Number | 0.5 | Medium active power (generating). Per unit value based on NP_P_MAX. | P p.u.
QP_CURVE_P1_GEN | Number | 0.2 | Lower active power (generating). Per unit value based on NP_P_MAX. | P p.u.
QP_CURVE_P1_LOAD | Number | -0.2 | Lower active power (absorbing). Per unit value based on NP_P_MAX_CHARGE. | P p.u.
QP_CURVE_P2_LOAD | Number | -0.5 | Medium active power (absorbing). Per unit value based on NP_P_MAX_CHARGE. | P p.u.
QP_CURVE_P3_LOAD | Number | -1 | Maximum active power (absorbing). Per unit value based on NP_P_MAX_CHARGE. | P p.u.
QP_CURVE_Q3_GEN | Number | -0.44 | Maximum reactive power while generating. Per unit value based on NP_Q_MAX_INJ or NP_Q_MAX_ABS. Negative signs should not be used but if present, indicates absorbing VAr. | VAr p.u.
QP_CURVE_Q2_GEN | Number | 0 | Medium reactive power while generating. Per unit value based on NP_Q_MAX_INJ or NP_Q_MAX_ABS. Negative signs should not be used but if present, indicates absorbing VAr. | VAr p.u.
QP_CURVE_Q1_GEN | Number | 0 | Lower reactive power while generating. Per unit value based on NP_Q_MAX_INJ or NP_Q_MAX_ABS. Negative signs should not be used but if present, indicates absorbing VAr. | VAr p.u.
QP_CURVE_Q1_LOAD | Number | 0 | Maximum reactive power while absorbing. Per unit value based on NP_Q_MAX_INJ or NP_Q_MAX_ABS. Negative signs should not be used but if present, indicates absorbing VAr. | VAr p.u.
QP_CURVE_Q2_LOAD | Number | 0 | Medium reactive power while absorbing. Per unit value based on NP_Q_MAX_INJ or NP_Q_MAX_ABS. Negative signs should not be used but if present, indicates absorbing VAr. | VAr p.u.
QP_CURVE_Q3_LOAD | Number | 0.44 | Lower reactive power while absorbing. Per unit value based on NP_Q_MAX_INJ or NP_Q_MAX_ABS. Negative signs should not be used but if present, indicates absorbing VAr. | VAr p.u.
PV_MODE_ENABLE | Select-list | Disabled | Voltage-active power mode enable |  | ENABLED/DISABLED | Volt-Watt Settings
PV_CURVE_V1 | Number | 1.06 | Upper start voltage for power reduction. Per unit value based on NP_AC_V_NOM (voltage base). | V p.u.
PV_CURVE_P1 | Number | 1 | Active power level at V1. Per unit value based on NP_P_MAX_CHARGE. | P p.u.
PV_CURVE_V2 | Number | 1.1 | Upper voltager for maximum power reduction. Per unit value based on NP_AC_V_NOM (voltage base). | V p.u.
PV_CURVE_P2_GEN | Number | Pmin | Minimum active power generating at V2. The lesser of 0.2*Prated or Pmin. Per unit value based on NP_P_MAX. | P p.u.
PV_CURVE_P2_LOAD | Number | 0 | Applicable to DER which can generate and absorb active power. Per unit Value based on NP_P_MAX_CHARGE. Negative values indicate active power load. Indicates maximum active power absorption. | P p.u.
PV_OLRT | Number | 10 | P(V) open loop response time setting | s
OV2_TRIP_V | Number | 1.2 | Must trip magnitude. Per unit value based on NP_AC_V_NOM (voltage base). | V p.u. |  | Voltage Trip Settings
OV2_TRIP_T | Number | 0.16 | Must trip duration | s
OV1_TRIP_V | Number | 1.1 | Must trip magnitude. Per unit value based on NP_AC_V_NOM (voltage base). | V p.u.
OV1_TRIP_T | Number | 13 | Must trip duration | s
UV1_TRIP_V | Number | 0.88 | Must trip magnitude. Per unit value based on NP_AC_V_NOM (voltage base). | V p.u.
UV1_TRIP_T | Number | 21 | Must trip duration | s
UV2_TRIP_V | Number | 0.5 | Must trip magnitude. Per unit value based on NP_AC_V_NOM (voltage base). | V p.u.
UV2_TRIP_T | Number | 2 | Must trip duration | s
OF2_TRIP_F | Number | 62 | Must trip frequency magnitude. Frequency values shall be reported to 3 decimal places. | Hz |  | Frequency Trip Settings
OF2_TRIP_T | Number | 0.16 | Must trip duration | s
OF1_TRIP_F | Number | 61.2 | Must trip frequency magnitude. Frequency values shall be reported to 3 decimal places. | Hz
OF1_TRIP_T | Number | 300 | Must trip duration | s
UF1_TRIP_F | Number | 58.5 | Must trip frequency magnitude. Frequency values shall be reported to 3 decimal places. | Hz
UF1_TRIP_T | Number | 300 | Must trip duration | s
UF2_TRIP_F | Number | 56.5 | Must trip frequency magnitude. Frequency values shall be reported to 3 decimal places. | Hz
UF2_TRIP_T | Number | 0.16 | Must trip duration | s
PF_DBOF | Number | 0.036 | Over frequency deadband offset from nominal frequency in Hz. Frequency values shall be reported to 3 decimal places. | Hz |  | Frequency Droop Settings
PF_DBUF | Number | 0.036 | Under frequency deadband offset from nominal frequency in Hz. Frequency values shall be reported to 3 decimal places. | Hz
PF_KOF | Number | 0.05 | Over frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop)
PF_KUF | Number | 0.05 | Under frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop)
PF_OLRT | Number | 5 | Frequency droop open loop response time. The duration from a step change in control signal input until the output changes by 90% of its final change, before any overshoot. | s
MC_HVRT_V2 | Number | 1.2 | High-voltage momentary cessation voltage. Per unit value based on NP_AC_V_NOM (voltage base). | V p.u. |  | Momentary Cessation Settings
MC_HVRT_T2 | Number | 13 | High-voltage momentary cessation time | s
MC_HVRT_V1 | Number | 1.1 | High-voltage momentary cessation voltage. Per unit value based on NP_AC_V_NOM (voltage base). | V p.u.
MC_HVRT_T1 | Number | 0 | High-voltage momentary cessation time | s
MC_LVRT_V1 | Number | 0.5 | Low-voltage momentary cessation voltage. Per unit value based on NP_AC_V_NOM (voltage base). | V p.u.
MC_LVRT_T1 | Number | 0 | Low-voltage momentary cessation time | s
MC_LVRT_V2 | Number | 0 | Low-voltage momentary cessation voltage. Per unit value based on NP_AC_V_NOM (voltage base). | V p.u.
MC_LVRT_T2 | Number | 2 | Low-voltage momentary cessation time | s

## DER_A_DSS
Name | OpenDSS | Notes | Reference: "Modeling High-Penetration PV for Distribution Interconnection Studies: Smart Inverter Function Modeling in OpenDSS, Rev. 2", EPRI, Palo Alto, CA: 2013. 3002002271. https://www.epri.com/research/products/3002002271
Trv
Trf
dbd1
dbd2
Kqv
Vref0
Tp
Tiq
Ddn
Dup
fdbd1
fdbd2
femax
femin
Pmax
Pmin
dPmax
dPmin
Tpord
Kpg
Kig
Imax
vl0
vl1
vh0
vh1
tvl0
tvl1
tvh0
tvh1
Vrfrac
fl
fh
tfl
tfh
Tg
rrpwr
Tv
Vpr
Pflag
Pqflag
Freq_flag
Ftripflag
Vtripflag
typeflag
Xe
Iqh1
Iql1
Vdip
Kiv
Tdb

## DER_A_GLD
Name | GridLAB-D | Notes | Reference: "GridLAB-D Inverter", [online] http://gridlab-d.shoutwiki.com/wiki/Inverter
Trv
Trf
dbd1
dbd2
Kqv
Vref0
Tp
Tiq
Ddn
Dup
fdbd1
fdbd2
femax
femin
Pmax
Pmin
dPmax
dPmin
Tpord
Kpg
Kig
Imax
vl0
vl1
vh0
vh1
tvl0
tvl1
tvh0
tvh1
Vrfrac
fl
fh
tfl
tfh
Tg
rrpwr
Tv
Vpr
Pflag
Pqflag
Freq_flag
Ftripflag
Vtripflag
typeflag
Xe
Iqh1
Iql1
Vdip
Kiv
Tdb

## IEEE1547.1_DSS
Param_Name | OpenDSS | Notes
NP_P_MAX | PVSystem.Pmpp
NP_P_MAX_OVER_PF
NP_OVER_PF
NP_P_MAX_UNDER_PF
NP_UNDER_PF
NP_VA_MAX | PVSystem.kva
NP_NORMAL_OP_CAT | n/a | Expressed in reactive power settings
NP_ABNORMAL_OP_CAT | n/a | Expressed in voltage trip settings
NP_INTENTIONAL_ISLAND_CAT | n/a | Behavior is usually IslandCapable
NP_Q_MAX_INJ | PVSystem.kvarLimit | Symmetrical in OpenDSS
NP_Q_MAX_ABS | PVSystem.kvarLimit | Symmetrical in OpenDSS
NP_P_MAX_CHARGE
NP_APPARENT_POWER_CHARGE_MAX
NP_AC_V_NOM | PVSystem.kV
NP_AC_V_MAX | PVSystem.Vmaxpu
NP_AC_V_MIN | PVSystem.Vminpu
NP_SUPPORTED_MODES |  | all but QP, use CONST_PF instead
NP_REACTIVE_SUSCEPTANCE | Load w/model = 2 | Constant Z load
NP_MANUFACTURER | n/a
NP_MODEL | n/a
NP_SERIAL_NUM | n/a | could encode into the name
NP_FW_VER | n/a
AP_LIMIT_P_ENABLE | n/a | Automate through a COM controller.
AP_MAX_P | n/a
ES_PERMIT_SERVICE | n/a | Automate through a COM controller.
ES_V_LOW | n/a
ES_V_HIGH | n/a
ES_F_LOW | n/a
ES_F_HIGH | n/a
ES_DELAY | n/a
ES_RANDOMIZED_DELAY | n/a
ES_RAMP_RATE | n/a
CONST_PF_MODE_ENABLE |  | Don’t attach InvControl or ExpControl
CONST_PF_EXCITATION | pf < 0 if absorbing Q | pf<0 actually means P and Q are opposite
CONST_PF | PVSystem.pf
CONST_Q_MODE_ENABLE |  | Don’t attach InvControl or ExpControl
CONST_Q | PVSystem.kvar
QV_MODE_ENABLE | InvControl.Mode=VOLTVAR | Or use ExpControl
QV_VREF | ExpControl.Vreg | Or InvControl.vvc_curve1
QV_VREF_AUTO_MODE | Use ExpControl | InvControl.LPFTau is not the same function
QV_VREF_OLRT | ExpControl.VregTau | ExpControl is limited to a single slope
QV_CURVE_V1 | InvControl.vvc_curve1.Xarray[1] | Add [0] at 0.5 pu voltage, Q1
QV_CURVE_Q1 | InvControl.vvc_curve1.Yarray[1]
QV_CURVE_V2 | InvControl.vvc_curve1.Xarray[2]
QV_CURVE_Q2 | InvControl.vvc_curve1.Yarray[2]
QV_CURVE_V3 | InvControl.vvc_curve1.Xarray[3]
QV_CURVE_Q3 | InvControl.vvc_curve1.Yarray[3]
QV_CURVE_V4 | InvControl.vvc_curve1.Xarray[4] | Add [5] at 1.5 pu voltage, Q4
QV_CURVE_Q4 | InvControl.vvc_curve1.Yarray[4]
QV_OLRT | InvControl.LPFTau = OLRT / 2.3026, or ExpControl.Tresponse = OLRT
QP_MODE_ENABLE | n/a | Approximate with CONST_PF
QP_CURVE_P1_GEN | n/a
QP_CURVE_P1_LOAD | n/a
QP_CURVE_P2_GEN | n/a
QP_CURVE_P2_LOAD | n/a
QP_CURVE_P3_GEN | n/a
QP_CURVE_P3_LOAD | n/a
QP_CURVE_Q1_GEN | n/a
QP_CURVE_Q1_LOAD | n/a
QP_CURVE_Q2_GEN | n/a
QP_CURVE_Q2_LOAD | n/a
QP_CURVE_Q3_GEN | n/a
QP_CURVE_Q3_LOAD | n/a
PV_MODE_ENABLE | InvControl.Mode=VOLTWATT
PV_CURVE_V1 | InvControl.voltwatt_curve.Xarray[1] | Add [0] at 0.5 pu voltage, P1
PV_CURVE_P1 | InvControl.voltwatt_curve.Yarray[1]
PV_CURVE_V2 | InvControl.voltwatt_curve.Xarray[2] | Add [3] at 1.5 pu voltage, P2
PV_CURVE_P2_GEN | InvControl.voltwatt_curve.Yarray[2]
PV_CURVE_P2_LOAD | InvControl.voltwatt_curve.Yarray[2] | will be < 0 in OpenDSS
PV_OLRT | InvControl.LPFTau = OLRT / 2.3026
OV2_TRIP_V | overvoltcurve.c_array[0] | In a relay with type=voltage, attached to the DER.
OV2_TRIP_T | overvoltcurve.t_array[0] | Set relay.kvbase to DER line-line or line-neutral.
OV1_TRIP_V | overvoltcurve.c_array[1] | Set SwitchedObj to the DER itself
OV1_TRIP_T | overvoltcurve.t_array[1] | Set SwitchedTerm to 1
UV1_TRIP_V | undervoltcurve.c_array[1] | Curve times increase monotonically.
UV1_TRIP_T | undervoltcurve.t_array[1]
UV2_TRIP_V | undervoltcurve.c_array[0]
UV2_TRIP_T | undervoltcurve.t_array[0]
OF2_TRIP_F | n/a | OpenDSS does not model frequency excursions.
OF2_TRIP_T | n/a
OF1_TRIP_F | n/a
OF1_TRIP_T | n/a
UF1_TRIP_F | n/a
UF1_TRIP_T | n/a
UF2_TRIP_F | n/a
UF2_TRIP_T | n/a
there is no PF_MODE_ENABLE, always on | n/a | OpenDSS does not model frequency excursions.
PF_DBOF | n/a
PF_DBUF | n/a
PF_KOF | n/a
PF_KUF | n/a
PF_OLRT | n/a
MC_HVRT_V2 | n/a | Could implement a new Relay mode
MC_HVRT_T2 | tbd
MC_HVRT_V1 | tbd
MC_HVRT_T1 | tbd
MC_LVRT_V1 | tbd
MC_LVRT_T1 | tbd
MC_LVRT_V2 | tbd
MC_LVRT_T2 | tbd

## IEEE1547.1_GLD
Param_Name | GridLAB-D | Notes
NP_P_MAX | solar.rated_power | Prefer solar.area and solar.weather
NP_P_MAX_OVER_PF | n/a
NP_OVER_PF | n/a
NP_P_MAX_UNDER_PF | n/a
NP_UNDER_PF | n/a
NP_VA_MAX | inverter.rated_power
NP_NORMAL_OP_CAT | n/a
NP_ABNORMAL_OP_CAT | n/a
NP_INTENTIONAL_ISLAND_CAT | n/a | Uncategorized, except for the grid-forming and grid-following inverter dynamic models
NP_Q_MAX_INJ | n/a
NP_Q_MAX_ABS | n/a
NP_P_MAX_CHARGE | n/a
NP_APPARENT_POWER_CHARGE_MAX | n/a
NP_AC_V_NOM | parent object's nominal_voltage | a node, meter, triplex_node or triplex_meter
NP_AC_V_MAX | n/a
NP_AC_V_MIN | n/a
NP_SUPPORTED_MODES |  | all but QP, use CONST_PF instead
NP_REACTIVE_SUSCEPTANCE | separate load object | use constant_impedance
NP_MANUFACTURER | n/a
NP_MODEL | n/a
NP_SERIAL_NUM | n/a | could encode into the name
NP_FW_VER | n/a
AP_LIMIT_P_ENABLE | n/a | Automate through FNCS or HELICS controller
AP_MAX_P | n/a
ES_PERMIT_SERVICE | n/a | Automate through FNCS or HELICS controller
ES_V_LOW | n/a
ES_V_HIGH | n/a
ES_F_LOW | n/a
ES_F_HIGH | n/a
ES_DELAY | inverter.reconnect_time
ES_RANDOMIZED_DELAY | n/a
ES_RAMP_RATE | n/a
CONST_PF_MODE_ENABLE | inverter.four_quadrant_control_mode=CONSTANT_PF, inverter.gen_mode=CONSTANT_PF | four_quadrant_control mode is the preferred implementation
CONST_PF_EXCITATION
CONST_PF | inverter.power_factor
CONST_Q_MODE_ENABLE | inverter.four_quadrant_control_mode=CONSTANT_PQ
CONST_Q | inverter.Q_Out
QV_MODE_ENABLE | inverter.four_quadrant_control_mode=VOLT_VAR
QV_VREF | inverter.V_base
QV_VREF_AUTO_MODE | n/a
QV_VREF_OLRT | n/a
QV_CURVE_V2 | inverter.V2
QV_CURVE_Q2 | inverter.Q2
QV_CURVE_V3 | inverter.V3
QV_CURVE_Q3 | inverter.Q3
QV_CURVE_V1 | inverter.V1
QV_CURVE_Q1 | inverter.Q1
QV_CURVE_V4 | inverter.V4
QV_CURVE_Q4 | inverter.Q4
QV_OLRT | n/a
QP_MODE_ENABLE | n/a | Approximate with CONSTANT_PF
QP_CURVE_P1_GEN | n/a
QP_CURVE_P1_LOAD | n/a
QP_CURVE_P2_GEN | n/a
QP_CURVE_P2_LOAD | n/a
QP_CURVE_P3_GEN | n/a
QP_CURVE_P3_LOAD | n/a
QP_CURVE_Q1_GEN | n/a
QP_CURVE_Q1_LOAD | n/a
QP_CURVE_Q2_GEN | n/a
QP_CURVE_Q2_LOAD | n/a
QP_CURVE_Q3_GEN | n/a
QP_CURVE_Q3_LOAD | n/a
PV_MODE_ENABLE | inverter.four_quadrant_control_mode=VOLT_WATT
PV_CURVE_V1 | inverter.VW_V1
PV_CURVE_P1 | inverter.VW_P1
PV_CURVE_V2 | inverter.VW_V2
PV_CURVE_P2_GEN | inverter.VW_P2
PV_CURVE_P2_LOAD | inverter.VW_P2 | will be < 0 in GridLAB-D
PV_OLRT | n/a
OV2_TRIP_V | inverter.over_voltage_high_cutout
OV2_TRIP_T | inverter.over_voltage_high_disconnect_time
OV1_TRIP_V | inverter.over_voltage_low_cutout
OV1_TRIP_T | inverter.over_voltage_low_disconnect_time
UV1_TRIP_V | inverter.under_voltage_high_cutout
UV1_TRIP_T | inverter.under_voltage_high_disconnect_time
UV2_TRIP_V | inverter.under_voltage_low_cutout
UV2_TRIP_T | inverter.under_voltage_low_disconnect_time
OF2_TRIP_F | inverter.over_freq_high_cutout | Must run in "delta mode"
OF2_TRIP_T | inverter.over_freq_high_disconnect_time
OF1_TRIP_F | inverter.over_freq_low_cutout
OF1_TRIP_T | inverter.over_freq_low_disconnect_time
UF1_TRIP_F | inverter.under_freq_high_cutout
UF1_TRIP_T | inverter.under_freq_high_disconnect_time
UF2_TRIP_F | inverter.under_freq_low_cutout
UF2_TRIP_T | inverter.under_freq_low_disconnect_time
there is no PF_MODE_ENABLE, always on | inverter.inverter_droop_fp=TRUE | Must run in "delta mode"
PF_DBOF | n/a - only droop gain (PF_KOF)
PF_DBUF | n/a - only droop gain (PF_KOF)
PF_KOF | inverter.R_fp | symmetrical in GridLAB-D
PF_KUF | inverter.R_fp
PF_OLRT | n/a
MC_HVRT_T1 | n/a | momentary cessation not modeled
MC_HVRT_T2 | tbd
MC_HVRT_V1 | tbd
MC_HVRT_V2 | tbd
MC_LVRT_T1 | tbd
MC_LVRT_T2 | tbd
MC_LVRT_V1 | tbd
MC_LVRT_V2 | tbd
Note on A19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure on this one. The deltamode model technically might have this in the Norton equivalent.
Note on A24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I couldnt' find either of these in the PDF you attached, so I'll just assume the FNCS/HELICS answer is right.
Note on B31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This value is associated with the UF/UV/OF/OV trip settings. I'm not sure what these ES values are, but since everything else is "N/A", I have no idea if this is right.
Note on B97: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Likely N/A - I have no idea what these are though.